## User Documentation
CSW Savings Calculator
2025-01-13 | date of last revision
version | 2.0.0
author | Solarc Energy Group
General: | This savings calculator generates separate savings for heating, HVAC auxiliaries and cooling based on a data set developed from parametric Energy Plus runs using prototype models
developed for and by BPA. Models address mid-sized offices, large offices, small hotels, large hotels, primary schools, secondary schools, small hospitals., mid-rise multifamily, and low-rise multifamily.
Several user inputs act as pointers to the proper subset of data. Adjustments to the data sub-set are made via regression equations to
account for differences in geography, climate, and HVAC operating hours (for offices), and average occupancy rate (for hotels). The dataset is representative of climate variations throughout United States climate zones.
Limitations: | This calculator is intended for use in building applications with existing single pane windows in the following building and representative electric and gas system types:
1) Mid-sized offices: Packaged VAV with electric reheat terminal units
2) Mid-sized offices: Packaged VAV with hydronic reheat from gas-fired boilers
3) Large offices: Built-up single duct VAV with hydronic reheat from electric resistance boilers.
4) Large offices: Built-up single duct VAV with hydronic reheat from gas-fired boilers.
5) Small hotels: Packaged terminal air conditioning (PTAC) units with electric heat
6) Small hotels: Packaged terminal heat pumps (PTHPs)
7) Large hotels: Distributed 4-pipe fan coil units with electric chiller and electric boiler
8) Large hotels: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler
9) Primary Schools: Single duct VAV with gas-fired hydronic reheat
10) Primary Schools: Single duct VAV with electric reheat
11) Primary Schools: Distributed 4-pipe fan coil units with electric chiller and electric boiler
12) Primary Schools: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler.
13) Secondary Schools: Single duct VAV with gas-fired hydronic reheat
14) Secondary Schools: Single duct VAV with electric reheat
15) Secondary Schools: Distributed 4-pipe fan coil units with electric chiller and electric boiler
16) Secondary Schools: Distributed 4-pipe fan coil units with electric chiller and gas-fired boiler.
17) Small Hospital: Single duct VAV with hydronic reheat from electric resistance boiler.
18) Small Hospital: Single duct VAV with hydronic reheat from gas-fired boiler.
19) Mid-rise Multifamily: Single zone fan coil units with electric hot water boiler and air-cooled chiller
20) Mid-rise Multifamily: Single zone fan coil units with gas-fired hot water boiler and air-cooled chiller
21) Low-rise Multifamily: Packaged terminal air conditioning units with electric heat
Instruction for use: | 1. All user input and savings output iresides in one of five building type tabs: Office, Hotel, School, Hospital, or Multifamily.
2. All user input cells contain a comment that provides guidance for the user. Depending on the building type there are (13) or (14) input cells.
3. All savings output cells are calculated and highlighted in yellow.
4. The user selects the closest geograhical location from a lists designating "State" and then "Cities", that then populates the degree-day cells.
Version Note: | This Beta version is populated with savings curves derived with Eplus model data for the building and system types listed above.
Input Cell Descriptions: | 1. Information About Your Project: Input project name, address, and contact information in locations as noted.
2. Project Location (State): This is a pull-down menu inpt. User must select one of 50 states and the District of Columbia.
3. Project Location (City): This is a pull-down menu input. User must select from the list of cities that are generated by the State selection. The list of cities corresponds to the cities for which typical meteorological climate data exist. User should select the city from the list that represents the nearest city to the project location. Selection of city populates the heating and cooling degree-day entries for the project.
4. Electric Utility: This is a text entry, and is not used in the savings calculation. User should enter the name of the servicing electric utility. This information is intended to support the development of an accurate estimate of electric rate.
5. Natural Gas Utility: This is a text entry, and is not used in the savings calculation. User should enter the name of the servicing natural gas utility. If there is no natural gas utility, then enter “N/A.” This information is intended to support the development of an accurate estimate of natural gas rate.
6. Electric Rate, $/kWh:This is a numerical entry and is used to determine electric cost savings, in dollars. The user should enter the cost of electrical energy in $ per kWh. Ideally, this should not include demand charges, utility surcharges, or other charges such as meter charges. It can include taxes or local charges that are assessed on the basis of monthly energy (kWh) use. In simple terms, this entry is intended to be derived by dividing a typical total monthly billing charge for energy only, in $, by the monthly electric energy use in that bill, in kWh. Note that electric rate schedules and billings can be complicated. Commercial accounts can include charges for peak monthly demand (kW), capacity charges, power factor penalties, meter charges, and other categories of charges. In addition, some rate schedules incorporate different rates depending upon time-of-use or magnitude of use (tiered rates). Most time-of use rates charge more for energy used during the utility peak times. Most tiered rates charge less for the highest tier of use. To make the most accurate estimate of energy cost savings, it is important to account for the cost of the electrical energy that will be most affected by the installation of CSW units. This cost is often referred to as the marginal electric rates. A simple way to estimate the marginal rate would be to divide the difference in two monthly billing charges by the difference in those two months energy use. For example, (Jan $ - Dec $) / (Jan kWh – Dec kWh).
7. Natural Gas Rate, $/therm: This is a numerical entry and is used to determine natural gas cost savings, in dollars. The user should enter the average annual cost of natural gas in $ per therm. This should not include utility surcharges, or other charges such as meter charges. In simple terms, this entry is intended to be derived by dividing a typical total monthly billing charge, in $, by the monthly natural gas energy use in that bill, in therms. If gas energy units are not therms, user should convert gas rate to the equivalent cost per therm. For example, gas rate at $6.00 per MMBtu (or deca-therm) would translate to an equivalent rate of $0.60 per therm. Similar to electric rates, some natural gas rate schedules incorporate different rates depending upon time-of-use or magnitude of use (tiered rates). Most time-of use rates charge more for energy used during the winter heating season. Most tiered rates charge slightly less for the highest tier of use. To make the most accurate estimate of energy cost savings, it is important to account for the cost of the natural gas energy that will be most affected by the installation of CSW units. This cost is often referred to as the marginal rate. A simple way to estimate the most applicable marginal rate would be to divide the difference in two wintertime monthly billing charges by the difference in those two months energy use. For example, (Jan $ - Dec $) / (Jan therms – Dec therms).
8. Building Area, Sq.Ft.:This is a numerical entry and is used to determine overall energy savings percentage, reported as Energy Use Intensities (in kBtu/sq.ft.-year.) It is also used to estimate overall peak cooling load reduction at an overall building level, in tons of refrigeration. It is also used in combination with the Number of floors input value, to estimate the window to wall ratio and alert the user when the CSW sq.ft. input may require verification. Building area should represent the conditioned area of all floors above grade. It is recommended to exclude basement area.
9. N o. of floors:This is a numerical whole number entry representing the total number of floors that are included in the Building Area entry. It is used in the logic to to estimate the window to wall ratio and alert the user when the CSW sq.ft. input may require verification. This entry does not directly affect energy savings. For Multifamily buildings, it is used to determine whether the project is Mid-rise (greater than 3 floors) or Low-rise (3 floors or less).
10. HVAC System Type: This is a pull-down menu input variable. The list of choices in the pull-down menu varies with the building type. User must select one of the entries from the pull-down menu (listed and briefly described below). The system type selection is used in the logic to determine the appropriate set of regression curves to reference for savings estimates.
a. Packaged VAV with electric reheat: This represents packaged rooftop variable air volume systems with electric resistance reheat coils in terminal units within ductwork. This is a typical HVAC system type for mid-rise office buildings. This system type can be selected for offices only of any size.
b. Packaged VAV with hydronic reheat: This represented packaged rooftop variable air volume systems with hydronic (hot water) reheat coils in terminal units within ductwork. This is a variation of typical HVAC systems for mid-rise office buildings where a gas-fired hot water boiler is installed in the building to meet system reheat needs. This system type can be selected for offices only of any size.
c. Built-up VAV with hydronic reheat from gas-fired boilers: This represents built-up variable air volume systems where air handling units and reheat coils are served by central chillers and boilers. Reheat coils in terminal units are hydronic (hot water). This is a typical HVAC system for large office buildings. This system type can be selected for offices only of any size.
d. Built-up VAV with hydronic reheat from electric resistance boilers: This represents built-up variable air volume systems where air handling units and reheat coils are served by electric-drive chillers and gas-fired boilers. Reheat coils in terminal units are hydronic (hot water). This is a typical HVAC system for large office buildings. This system type can be selected for offices of any size.
e. Packaged Terminal Air Conditioner (PTAC): This system is common for small hotels and assumes electric resistance heat. It can be selected for hotels only of any size, or low-rise multifamily.
f. Packaged Terminal Heat Pump (PTHP): This system is common for small hotels, or motels. Heating fuel is electricity via electric-drive heat pumps. It can be selected for hotels only of any size.
g. Distributed 4-pipe fan coil units (FCUs) with electric chiller and electric boiler: This system type assumes a 4-pipe hydronic distribution system serving distributed fan coil units from a central plant with electric-drive chiller and electric resistance boiler. It can be selected for hotels, schools of any size, or mid-rise multifamily.
h. Distributed 4-pipe fan coil units (FCUs) with electric chiller and gas-fired boiler: This system type assumes a 4-pipe hydronic distribution system serving distributed fan coil units from a central plant with electric-drive chiller and gas-fired boiler. It can be selected for hotels, schools of any size, or mid-rise multifamily.
i. Central Ducted VAV with gas-fired reheat: This system represented a centralized, built-up VAV system served by a 4-pipe hydronic systems for heating and cooling. A central plant with electric-drive chiller and gas-fired boiler provides the hydronic cooling and heat. It can be selected for schools or hospitals of any size.
j. Central Ducted VAV with electric resistance reheat: This system represented a centralized, built-up VAV system served by a 4-pipe hydronic systems for heating and cooling. A central plant with electric-drive chiller and anelectric resistance boiler boiler provides the hydronic cooling and heat. It can be selected for schools or hospitals of any size.
k. Other: This selection should be made for any HVAC system types that does not fit into one of the categories listed above. Note that even if this selection is made, savings will be based on simulations that assume one of the system types listed above.
11. Dominant Heating Fuel:This is a pull-down menu input variable. User must select one of the three entries from the pull-down menu – electric, natural gas, or none. This entry will be used in the logic that determines the set of regression equations to be used to estimate heating savings. For hotels and lowrise multifamily, this entry is overridden to electric if the system type chosen is PTAC or PTHP. For offices, this entry is overridden to electric if the system type chosen is Packaged VAV with Electric Reheat. If "none" is selected, savings for heating will be zero.
12. Cooling Installed?: This is a pull-down menu input variable. User must select either "yes" or "no." If "no" is selected, cooling savings for will be adjusted to reflect HVAC auxiliary savings only.
13. Tpe of Existing Window: This is a pull-down menu inpt. User must select one of the two entries from the pull-down menu - single or double. Single represents windows wth single pane clear glass (U-value of 1.04 Btu/hr-SF-F and solar heat gain coefficient (SHGC) of 0.73). Double represents windows with double pane clear glass (U-value of 0.57 Btu/hr-SF-F and SHGC of 0.63).
14. Type of CSW Analyzed: This is a pull-down menu input that is dependent upon the type of existing window selected. User must select one of the two entries from the pull-down menu - single or double. Note that for double pane existing windows, the only selection in single. Single represents single pane CSW product lines, and is the most common type of CSW product in the current market. Savings reported in this calculator for single pane CSW (in combination with single pane primary window) assume that improved window U-value of 0.47 Btu/hr-SF-F and improved window solar heat gain coeefiecient (SHGC) of 0.57. Savings reported in this calculator for single pane CSW (in combination with double pane primary window) assume that improved window U-value of 0.40 Btu/hr-SF-F and improved window solar heat gain coefiecient (SHGC) of 0.47. Double represents double pane CSW product lines. Savings reported in this calculator for double pane CSW (in combination with a single pane primary window) assume that improved window U-value of 0.37 Btu/hr-SF-F and improved window solar heat gain coeefiecient (SHGC) of 0.32. This entry will be used in the logic that determines the set of regression equations to be used to estimate savings.
15. Sq.Ft. of CSW Installed: This is a numerical entry representing the total area, in sq.ft. of CSW units being considered for installation. The input is not limited to a minimum or a maximum value. However, if a value less than zero is input, negative savings will be reported. This is not a relevant answer, therefore a negative number should not be input. If an excessively large number is input that results in an estimated window to wall ratio greater than 50%, a user alert will be generated, “Warning: Sq.Ft of CSW Installed Appears Larger than Practical for this Building Size.”
Special Input Cells: | For offices only: Annual Operating Hours: This is a numerical whole number entry with limits defined. Minimum entry is 1986 hours per year. Maximum entry is 8760 hours per year, representing continuous operation. Entry is the number of HVAC operating hours per year, averaged for the entire building.
For hotels only: Ave. Occupancy Rate: This is a percentage entry that represents that average annual occupancy rate of the hotel. It has implicit limits. Any entry less than 33% will use 33% in the savings logic. Entries above 100% will use 100% in the savings logic. Entries between 33% and 100% will interpolate between minimum and maixmum savings factors.
For schools only: Building Type: This is a pull-down menu selection that allows user to select Primary or Secondary School type.
For multifamily only: Infiltration Savings: This is a pull-down menu selection that allows user to select "Included" or "Excluded". If infiltraton savings is included, then estimated savings includes a benefit associated with reduced perimeter zone infiltration. If excluded, reported savings will be adjusted to reflect savings based only on improved window U-value and SHGC.

## Office
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Large Office | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Example, 250,000 SF, 10-story Office
Project Address | Street | City, State | Zip Code
New York, NY
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 212358.9268
Annual Natural Gas Energy Savings, therms/yr |  |  | 22419.0841
Annual Energy Cost Savings, $/year |  |  | 70128.2356
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 96.9029
Savings, % and kBtu/SF-year: |  | 12.25% | 11.8668
Information About Your Building Location |  | Information About Your Building | [10 empty] | 0
|  | Building Type | Office
Project Location (State) | New_York | Building Area, Sq.Ft. | 250000 | Minimum office size limit is approximately 15,000 sq.ft. Maximum office size limit is approximately 500,000 sq.ft.
Project Location (City) | New York | No. of Floors | 10 | Mid-size offices are typically 3 floors or less in height.
Electric Utility | Con Edison | HVAC System Type | Built-up VAV with hydronic reheat | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | Con Edison | Heating Fuel | Natural Gas | For packaged VAV options, make sure the fuel type is consistent with the system choice, especially for electric reheat (fuel type=electric.) | [8 empty] | SingleSingleMidOfficePVAV_ElecElectricLo
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [7 empty] | Savings Factors |  |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 4885 | Annual Operating Hours | 4000 | Minimum input is 1980 hours/yr. Maximum input is 8760 hours/yr. |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | Hours | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 1133 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | Hi | Single | Single | Large | Office | VAV | Natural Gas | 8760 | SingleSingleLargeOfficeVAVNatural Gas8760 | 0 | 12.2721 | 1.442 | 147.5656 | 1 | 96.9029 | 0 | 557.581 | 0 | Baseline
|  | Information About Your Proposed CSW Project |  |  | Lo | Single | Single | Large | Office | VAV | Natural Gas | 2912 | SingleSingleLargeOfficeVAVNatural Gas2912 | 0 | 5.8916 | 0.58852 | 85.3228 |  | 85.0361 | 11.8668 | 510.1056 | 47.4754 | CSW
Information About Your Building |  | Type of CSW Analyzed | Single | Do not select double pane secondary windows added to double pane primary windows. | [14 empty] | % | 0.12246 |  | 0.085145
Electric Rate, $/kWh | 0.25 | Sq.ft. of CSW Installed | 30000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0.76 | Est. Window Wall Ratio | 0.31623
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 212358.9268
Cooling & Fans, kWh/SFCSW | 7.0786
Heating, therms/SFcSW | 0.7473 | Gas Savings, therms/yr | 22419.0841
Electric Cost Savings, $/yr | 53089.7317 | Total Savings, kBtu/SF-yr | 11.8668
Gas Cost Savings, $/yr | 17038.5039 | Total Savings, $/yr | 70128.2356
Annual Percentage Total Energy Savings |  |  | 12.25%
Percentage HVAC Downsize |  |  | 8.515%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S. states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry including basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing electric utility.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F22: Select "No" if there is no cooling system installed.
Note on F23: Enter average annual operating hours for HVAC system. Include hours that system operates at night or in other unoccupied periods.
Note on F24: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Hotel
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Small Hotel | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Royal Hawaiian Example
Project Address | Street | City, State | Zip Code
Honolulu HI
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 206973.1523
Annual Natural Gas Energy Savings, therms/yr |  |  | 0
Annual Energy Cost Savings, $/year |  |  | 78649.7979
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 56.6865
Savings, % and kBtu/SF-year |  | 7.788% | 4.415
Information About Your Building Location |  | Information About Your Building | [11 empty] | 0
|  | Building Type | Small Hotel
Project Location (State) | Hawaii | Building Area, Sq.Ft. | 160000 | Minimum small hotel size limit is approximately 15,000 sq.ft. Maximum size limit is approximately 250,000 sq.ft.
Project Location (City) | Honolulu | No. of Floors | 2
Electric Utility | Hawaiian Electric | HVAC System Type | PTHP | PTAC or PTHP choice will default to Small Hotel regardless of building area input. Fan Coil Unit or Other choice will default to large hotel regardless of building area input.
Natural Gas Utility | N/A | Dominant Heating Fuel | Natural Gas | For PTAC, PTHP, or Other system types, fuel type defaults to electric for savings estimates.
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [8 empty] | Savings Factors |  |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 0 | Ave. Occupancy Rate | 100% | Typical occupancy rate is between 50% to 100%. For savings estimates, occupancy rates between 33% and 100% are used. |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | PTHP HDD | Occ | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 4561 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | High | Single | Double | Small | Hotel | PTHP | Electric | Low | 100 | SingleDoubleSmallHotelPTHPElectricLow100 | 0.19401 | 13.6042 | 0 | 56.6865 | 1 | 56.6865 | 0 | 378.7297 | 0 | Baseline
|  | Information About Your Proposed CSW Project |  |  | Low | Single | Double | Small | Hotel | PTHP | Electric | Low | 33 | SingleDoubleSmallHotelPTHPElectricLow33 | 0.15066 | 11.2244 | 0 | 50.7112 |  | 52.2715 | 4.415 | 310.3567 | 68.373 | CSW
Information About Your Building |  | Type of CSW Analyzed | Double | Do not select double pane secondary windows added to double pane primary windows. | [15 empty] | % | 0.077884 |  | 0.18053
Electric Rate, $/kWh | 0.38 | Sq.ft. of CSW Installed | 15000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0 | Est. Window Wall Ratio | 0.44194
Savings Output
Heating, kWh/SFCSW | 0.19401 | Electric Savings, kWh/yr | 206973.1523
Cooling & Fans, kWh/SFCSW | 13.6042
Heating, therms/SFCSW | 0 | Gas Savings, therms/yr | 0
Electric Cost Savings, $/yr | 78649.7979 | Total Savings, kBtu/SF-yr | 4.415
Gas Cost Savings, $/yr | 0 | Total Savings, $/yr | 78649.7979
Annual Percentage Total Energy Savings |  |  | 7.788%
Percentage HVAC Downsize |  |  | 18.05%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance or heat pump systems, select "electric."
Note on F22: For electric resistance heating only systems, select "No."
Note on F23: Enter average annual occupancy rate.
Note on F24: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## School
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Secondary School | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | 300000 SF High School Example
Project Address | Street | City, State | Zip Code
Salt Lake City UT
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 65007.9251
Annual Natural Gas Energy Savings, therms/yr |  |  | 7730.5222
Annual Energy Cost Savings, $/year |  |  | 7888.7095
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 82.2746
Savings, % and kBtu/SF-year |  | 4.031% | 3.3164
Information About Your Building Location |  | Information About Your Building | [9 empty] | 0
|  | Building Type | Secondary School | Select school type - primary (elementary) or secondary (middle or high school).
Project Location (State) | Utah | Building Area, Sq.Ft. | 300000 | Minimum school size limit is approximately 25,000 sq.ft. Maximum size limit is approximately 350,000 sq.ft.
Project Location (City) | Salt Lake City | No. of Floors | 2
Electric Utility | Rocky Mountain Power | HVAC System Type | Central Ducted VAV | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | Enbridge Gas | Dominant Heating Fuel | Natural Gas
|  | Cooling Installed? | Yes |  | Lookup Key | [7 empty] | Savings Factors |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 5350 | Type of Existing Window | Double pane | U-assembly = 0.57 Btu/hr-SF-F; SHGC = 0.63 | Base | CSW Type | Building Type | HVAC System Type | Fuel | Location | Occ | LU Conc | H, kWh | C, kWh | H, therms | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 1118 |  |  |  | Double | Single | SS | VAV | Natural Gas |  |  | DoubleSingleSSVAVNatural Gas | 0 | 4.3339 | 0.51537 | 1 | 82.2746 | 0 | 431.4394 | 0 | Baseline
|  | Information About Your Proposed CSW Project | [14 empty] | 78.9582 | 3.3164 | 411.8439 | 19.5955 | CSW
Information About Your Building |  | Type of CSW Analyzed | Single | Double pane secondary windows are a valid entry only for buildings with existing single pane windows. | [12 empty] | % | 0.040309 |  | 0.045419
Electric Rate, $/kWh | 0.05 | Sq.ft. of CSW Installed | 15000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0.6 | Est. Window Wall Ratio | 0.32275
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 65007.9251
Cooling & Fans, kWh/SFCSW | 4.3339
Heating, therms/SFCSW | 0.51537 | Gas Savings, therms/yr | 7730.5222
Electric Cost Savings, $/yr | 3250.3963 | Total Savings, kBtu/SF-yr | 3.3164
Gas Cost Savings, $/yr | 4638.3133 | Total Savings, $/yr | 7888.7095
Annual Percentage Total Energy Savings |  |  | 4.031%
Percentage HVAC Downsize |  |  | 4.542%
Note on C4: Identify individual project name and/or calculation run.
Note on F17: Select school type.
Note on C18: Select appropriate state from list of Pacific Northwest states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F23: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Hospital
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Hospital | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Small Hospital Example
Project Address | Street | City, State | Zip Code
Walla Walla WA
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 188469.3571
Annual Natural Gas Energy Savings, therms/yr |  |  | 18037.5776
Annual Energy Cost Savings, $/year |  |  | 27483.0092
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 230.1992
Savings, % and kBtu/SF-year |  | 5.062% | 11.6524
Information About Your Building Location |  | Information About Your Building
|  | Building Type | Hospital
Project Location (State) | Washington | Building Area, Sq.Ft. | 210000 | Minimum size limit for small hospital is approximately 30,000 sq.ft. Maximum size limit is approximately 300,000 sq.ft.
Project Location (City) | Walla Walla | No. of Floors | 4
Electric Utility | Pacific Power | HVAC System Type | Central Ducted VAV | For heat pumps, adjustment of electrical heating savings is warranted. See user documentation.
Natural Gas Utility | NWN | Dominant Heating Fuel | Natural Gas
|  | Cooling Installed? | Yes |  | Lookup Key | [7 empty] | Savings Factors |  |  | Clg | Graphics Drivers
Location HDD (Base 65) | 4836 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 | Base | CSW Type | Building Type | HVAC System Type | Fuel | Location | Occ | LU Conc | H, kWh | C, kWh | H, therms | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 839 |  |  |  | Single | Double | Hosp | VAV | Natural Gas |  |  | SingleDoubleHospVAVNatural Gas | 0 | 15.7058 | 1.5031 | 1 | 230.1992 | 0 | 365.1315 | 0 | Baseline
|  | Information About Your ProposedCSW Project | [14 empty] | 218.5468 | 11.6524 | 340.8423 | 24.2892 | CSW
Information About Your Building |  | Type of CSW Analyzed | Double | Double pane secondary windows are a valid entry only for buildings with existing single pane windows. | [12 empty] | % | 0.050619 |  | 0.066522
Electric Rate, $/kWh | 0.075 | Sq.ft. of CSW Installed | 12000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such thatWWR is 0.25.
Natural Gas Rate, $/therm | 0.74 | Est. Window Wall Ratio | 0.21822
Savings Output
Heating, kWh/SFCSW | 0 | Electric Savings, kWh/yr | 188469.3571
Cooling & Fans, kWh/SFCSW | 15.7058
Heating, therms/SFCSW | 1.5031 | Gas Savings, therms/yr | 18037.5776
Electric Cost Savings, $/yr | 14135.2018 | Total Savings, kBtu/SF-yr | 11.6524
Gas Cost Savings, $/yr | 13347.8074 | Total Savings, $/yr | 27483.0092
Annual Percentage Total Energy Savings |  |  | 5.062%
Percentage HVAC Downsize |  |  | 6.652%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of Pacific Northwest states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance reheat systems, select "electric."
Note on F23: Enter dominant type of existnig window
Note on F26: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C27: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F27: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C28: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Multi-family
COMMERCIAL SECONDARY WINDOWS SAVINGS CALCULATOR |  |  | Low-rise Multifamily | User Notes / Guidelines / Warnings
Ver. 2.0.0 |  |  | 2025-01-13 | User input notes are indicated by red triangles in select cells. Hover to read on-line help. Detailed input guidelines are provided in the User Documentaiton tab and in the dynamic cells below.
Information About Your Project
Project Name | Low Rise Apartment Example
Project Address | Street | City, State | Zip Code
Raliegh NC
Contact Information | Name | Phone | Email
Annual Electric Energy Savings, kWh/yr |  |  | 73952.5251
Annual Natural Gas Energy Savings, therms/yr |  |  | 0
Annual Energy Cost Savings, $/year |  |  | 12571.9293
Baseline Energy Use Intensity, kBtu/SF-year |  |  | 9.3268
Savings, % and kBtu/SF-year |  | 28.38% | 12.62
Information About Your Building Location |  | Information About Your Building | [9 empty] | 0
|  | Building Type | Low-rise Multifamily
Project Location (State) | North_Carolina | Building Area, Sq.Ft. | 20000 | Minimum multi-family size limit is approximately 10,000 sq.ft. Maximum size limit is approximately 150,000 sq.ft.
Project Location (City) | Raleigh | No. of Floors | 2 | Mid-size multi-family buildings are designated for all buildings 4 floors and above.
Electric Utility | Duke Energy | HVAC System Type | PTAC | Savings estimated for Low-rise assume Packaged terminal air conditioner (PTAC) system. Savings for Mid-rise assume Fan coil unit (FCU) system.")
Natural Gas Utility | N/A | Dominant Heating Fuel | Electric | [13 empty] | Heat | Cool
|  | Cooling Installed? | Yes | Savings includes reduction in mechanical cooling. |  | Lookup Key & Interpolation Factors | [6 empty] | Savings Factors |  |  |  | Infil | Infil | Clg | Graphics Drivers
Location HDD (Base 65) | 3465 | Type of Existing Window | Single pane | U-assembly = 1.03 Btu/hr-SF-F; SHGC = 0.73 |  | Base | CSW Type | Size | Building Type | HVAC System Type | Fuel | LU Conc | H, kWh | C, kWh | H, therms | EUI | Factor | Factor | Factor | EUI |  | Peak Clg Ld
Location CDD (Base 65) | 1566 | Infiltration Savings | Included | Savings includes contribution of reduced air leakage.
[5 empty] | High | Single | Single | Low | MF | PTAC | Electric | SingleSingleLowMFPTACElectric | 9.3268 | 5.4637 | 0 | 44.472 | 1 | 1 | 1 | 44.472 | 0 | 28.263 | 0 | Baseline
|  | Information About Your Proposed CSW Project | [17 empty] | 31.852 | 12.62 | 15.0498 | 13.2132 | CSW
Information About Your Building |  | Type of CSW Analyzed | Single | Do not select double pane secondary windows added to double pane primary windows. | [15 empty] | % | 0.28377 |  | 0.46751
Electric Rate, $/kWh | 0.17 | Sq.ft. of CSW Installed | 5000 | Typical building Window-Wall Ratio (WWR) is between 0.1-0.5. If unsure about actual CSW Sq.Ft., input CSW area such that WWR is 0.25.
Natural Gas Rate, $/therm | 0 | Est. Window Wall Ratio | 0.41667
Savings Output
Heating, kWh/SFCSW | 9.3268 | Electric Savings, kWh/yr | 73952.5251
Cooling & Fans, kWh/SFCSW | 5.4637
Heating, therms/SFCSW | 0 | Gas Savings, therms/yr | 0
Electric Cost Savings, $/yr | 12571.9293 | Total Savings, kBtu/SF-yr | 12.62
Gas Cost Savings, $/yr | 0 | Total Savings, $/yr | 12571.9293
Annual Percentage Total Energy Savings |  |  | 28.38%
200
Percentage HVAC Downsize |  |  | 46.75%
Note on C4: Identify individual project name and/or calculation run.
Note on C18: Select appropriate state from list of U.S. states.
Note on F18: Enter the area of the building that is heated or cooled.
Note on C19: Select city that is closest (geographically) to project location.
Note on F19: Enter number of floors contributing to building area entry excluding basement floors.
Note on C20: Enter name of servicing electric utility.
Note on F20: Select the HVAC system type that best matches predominant system type.
Note on C21: Enter name of servicing gas utility, if any.
Note on F21: Insert predominant heating fuel. For electric resistance heat including PTAC systems, select "electric."
Note on F23: Enter the dominent type of existing window.
Note on F24: Indicate whether savings due to reduced infiltration is to be included.
Note on F27: Select type of CSW system proposed for installation. Single=single pane CSW. Double=double pane CSW.
Note on C28: Input melded rate, $/kWh that includes both energy (kWh) charge and demand (kW) charge.
Note on F28: Enter the sq.ft. of CSW units proposed to be installed in the building. Include all units in a total figure.
Note on C29: Enter average annual gas rate, in $/therm. If the building does not heat with gas, enter zero.

## Savings Lookup
Savings Look-up Tables (using Regression Equations with HDD/CDD as independent variables)
[9 empty] | Savings |  |  |  |  | EUI |  |  |  | Loads | Loads
[9 empty] | Electric Savings, kWh/SF |  | Gas Savings, therms/SF |  | Regression_Done | Base_EUI | CSW_EUI | Percent | Regression_Done | Baseline Peak Cooling | Clg Load Reduced | Htg Load Reduced | Baseline Peak Cooling | Base Clg Load | CSW Ld Red | CSW Ld Red | CWS Clg Load | Regression_done | Infil Savings Reduction Factors |  | Cool Adjust
Base | CSW_Type | Building_Size | Building_Type | HVAC_System_Type | Fuel_Type | PTHP | Hours | Look-up_Conc | Electric_savings_Heat_kWhperSF | electric_savings_Cooling_and_Aux_kWhperSF | Gas_savings_Heat_thermsperSF |  |  | Base_EUI_kBtuperSFperyr | CSW_EUI_kBtuperSFperyr | Percent | Regression_Done | baseline_peak_cooling_BtuhperSF | Clg_Load_reduced_BtuhperSF | htg_load_reduced_BtuhperSF | baseline_peak_cooling_Btuh | base_cooling_load_Tons | CSW_ld_red_Btuh | csw_ld_red_Tons | CWS_Clg_load_Tons |  | infiltration_savings_reduction_factors_Heat | infiltration_reduction_factors_Cool | Cool_adjust
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 2080 | SingleSingleMidOfficePVAV_ElecElectric2080 | 7.6688 | 3.0292 | 0 |  | Y | 51.0964 | 39.2297 | 23.22% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 2912 | SingleSingleMidOfficePVAV_ElecElectric2912 | 10.9155 | 4.986 | 0 |  | Y | 60.166 | 48.2993 | 19.72% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203
Single | Single | Mid | Office | PVAV_Elec | Electric |  | 8760 | SingleSingleMidOfficePVAV_ElecElectric8760 | 27.0246 | 10.4071 | 0 |  | Y | 128.5889 | 116.7222 | 9.228% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 2080 | SingleDoubleMidOfficePVAV_ElecElectric2080 | 7.1234 | 5.3282 | 0 |  | Y | 51.0964 | 39.2297 | 23.22% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 2912 | SingleDoubleMidOfficePVAV_ElecElectric2912 | 10.3101 | 7.9887 | 0 |  | Y | 60.166 | 48.2993 | 19.72% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203
Single | Double | Mid | Office | PVAV_Elec | Electric |  | 8760 | SingleDoubleMidOfficePVAV_ElecElectric8760 | 28.3897 | 13.2929 | 0 |  | Y | 128.5889 | 116.7222 | 9.228% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 2080 | DoubleSingleMidOfficePVAV_ElecElectric2080 | 3.4877 | 2.1054 | 0 |  | Y | 47.81 | 35.9433 | 24.82% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 2912 | DoubleSingleMidOfficePVAV_ElecElectric2912 | 4.6262 | 3.1044 | 0 |  | Y | 55.5401 | 43.6733 | 21.37% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203
Double | Single | Mid | Office | PVAV_Elec | Electric |  | 8760 | DoubleSingleMidOfficePVAV_ElecElectric8760 | 13.1367 | 5.1491 | 0 |  | Y | 115.8634 | 103.9966 | 10.24% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | SingleSingleMidOfficePVAV_GasNatural Gas2080 | 0 | 3.0292 | 0.37448 |  | Y | 57.1771 | 45.3104 | 20.75% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | SingleSingleMidOfficePVAV_GasNatural Gas2912 | 0 | 4.986 | 0.53194 |  | Y | 78.0253 | 66.1585 | 15.21% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203
Single | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | SingleSingleMidOfficePVAV_GasNatural Gas8760 | 0 | 10.4071 | -2.8646 |  | Y | 156.5864 | 144.7197 | 7.578% | Y | 23.2732 | 27.2766 |  | 5818308.3697 | 484.859 | 818296.723 | 68.1914 | 416.6676 | Y |  |  | 0.61203
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | SingleDoubleMidOfficePVAV_GasNatural Gas2080 | 0 | 5.3282 | 0.34688 |  | Y | 57.1771 | 45.3104 | 20.75% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | SingleDoubleMidOfficePVAV_GasNatural Gas2912 | 0 | 7.9887 | 0.50268 |  | Y | 78.0253 | 66.1585 | 15.21% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203
Single | Double | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | SingleDoubleMidOfficePVAV_GasNatural Gas8760 | 0 | 13.2929 | 1.3828 |  | Y | 156.5864 | 144.7197 | 7.578% | Y | 23.2732 | 55.2981 |  | 5818308.3697 | 484.859 | 1658943.1321 | 138.2453 | 346.6138 | Y |  |  | 0.61203
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2080 | DoubleSingleMidOfficePVAV_GasNatural Gas2080 | 0 | 2.1054 | 0.16957 |  | Y | 47.8279 | 35.9612 | 24.81% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 2912 | DoubleSingleMidOfficePVAV_GasNatural Gas2912 | 0 | 3.1044 | 0.2249 |  | Y | 55.3919 | 43.5252 | 21.42% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203
Double | Single | Mid | Office | PVAV_Gas | Natural Gas |  | 8760 | DoubleSingleMidOfficePVAV_GasNatural Gas8760 | 0 | 5.1491 | 0.63825 |  | Y | 115.8848 | 104.0181 | 10.24% | Y | 20.6646 | 19.1755 |  | 5166160.9059 | 430.5134 | 575264.6378 | 47.9387 | 382.5747 | Y |  |  | 0.61203
Single | Single | Large | Office | VAV | Electric |  | 2080 | SingleSingleLargeOfficeVAVElectric2080 | 8.3768 | 3.5966 | 0 |  | Y | 52.0782 | 40.2114 | 22.79% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996
Single | Single | Large | Office | VAV | Electric |  | 2912 | SingleSingleLargeOfficeVAVElectric2912 | 12.0673 | 5.8916 | 0 |  | Y | 79.0511 | 67.1843 | 15.01% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996
Single | Single | Large | Office | VAV | Electric |  | 8760 | SingleSingleLargeOfficeVAVElectric8760 | 29.5821 | 12.2721 | 0 |  | Y | 137.2754 | 125.4086 | 8.644% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996
Single | Double | Large | Office | VAV | Electric |  | 2080 | SingleDoubleLargeOfficeVAVElectric2080 | 7.7938 | 6.3007 | 0 |  | Y | 52.0782 | 40.2114 | 22.79% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996
Single | Double | Large | Office | VAV | Electric |  | 2912 | SingleDoubleLargeOfficeVAVElectric2912 | 11.2347 | 9.421 | 0 |  | Y | 79.0511 | 67.1843 | 15.01% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996
Single | Double | Large | Office | VAV | Electric |  | 8760 | SingleDoubleLargeOfficeVAVElectric8760 | 31.2095 | 15.6912 | 0 |  | Y | 137.2754 | 125.4086 | 8.644% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996
Double | Single | Large | Office | VAV | Electric |  | 2080 | DoubleSingleLargeOfficeVAVElectric2080 | 3.8329 | 2.4676 | 0 |  | Y | 106.8943 | 95.0275 | 11.1% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996
Double | Single | Large | Office | VAV | Electric |  | 2912 | DoubleSingleLargeOfficeVAVElectric2912 | 5.0846 | 3.6288 | 0 |  | Y | 73.4438 | 61.577 | 16.16% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996
Double | Single | Large | Office | VAV | Electric |  | 8760 | DoubleSingleLargeOfficeVAVElectric8760 | 14.3964 | 6.0331 | 0 |  | Y | 123.8742 | 112.0074 | 9.58% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996
Single | Single | Large | Office | VAV | Natural Gas |  | 2080 | SingleSingleLargeOfficeVAVNatural Gas2080 | 0 | 3.5966 | 0.40825 |  | Y | 53.3199 | 41.4531 | 22.26% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996
Single | Single | Large | Office | VAV | Natural Gas |  | 2912 | SingleSingleLargeOfficeVAVNatural Gas2912 | 0 | 5.8916 | 0.58852 |  | Y | 85.3228 | 73.4561 | 13.91% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996
Single | Single | Large | Office | VAV | Natural Gas |  | 8760 | SingleSingleLargeOfficeVAVNatural Gas8760 | 0 | 12.2721 | 1.442 |  | Y | 147.5656 | 135.6989 | 8.042% | Y | 26.7639 | 18.9902 |  | 6690972.2365 | 557.581 | 569704.5371 | 47.4754 | 510.1056 | Y |  |  | 0.79996
Single | Double | Large | Office | VAV | Natural Gas |  | 2080 | SingleDoubleLargeOfficeVAVNatural Gas2080 | 0 | 6.3007 | 0.37827 |  | Y | 53.3199 | 41.4531 | 22.26% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996
Single | Double | Large | Office | VAV | Natural Gas |  | 2912 | SingleDoubleLargeOfficeVAVNatural Gas2912 | 0 | 9.421 | 0.54512 |  | Y | 85.3228 | 73.4561 | 13.91% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996
Single | Double | Large | Office | VAV | Natural Gas |  | 8760 | SingleDoubleLargeOfficeVAVNatural Gas8760 | 0 | 15.6912 | 1.5209 |  | Y | 147.5656 | 135.6989 | 8.042% | Y | 26.7639 | 57.9269 |  | 6690972.2365 | 557.581 | 1737806.061 | 144.8172 | 412.7638 | Y |  |  | 0.79996
Double | Single | Large | Office | VAV | Natural Gas |  | 2080 | DoubleSingleLargeOfficeVAVNatural Gas2080 | 0 | 2.4676 | 0.18581 |  | Y | 53.1479 | 41.2812 | 22.33% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996
Double | Single | Large | Office | VAV | Natural Gas |  | 2912 | DoubleSingleLargeOfficeVAVNatural Gas2912 | 0 | 3.6288 | 0.24747 |  | Y | 80.12 | 68.2532 | 14.81% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996
Double | Single | Large | Office | VAV | Natural Gas |  | 8760 | DoubleSingleLargeOfficeVAVNatural Gas8760 | 0 | 6.0331 | 0.70013 |  | Y | 131.0398 | 119.1731 | 9.056% | Y | 24.7202 | 21.267 |  | 6180047.5912 | 515.004 | 638011.3343 | 53.1676 | 461.8364 | Y |  |  | 0.79996
Single | Single | Small | Hotel | PTAC | Electric |  | 33 | SingleSingleSmallHotelPTACElectric33 | 0.26195 | 6.0461 | 0 | 0.033529 | Y | 53.3842 | 48.9692 | 8.27% | Y | 28.4047 | 29.6018 |  | 4544756.6023 | 378.7297 | 444027.4853 | 37.0023 | 341.7274 | Y |  |  | #REF!
Single | Single | Small | Hotel | PTAC | Electric |  | 100 | SingleSingleSmallHotelPTACElectric100 | 0.34628 | 7.2822 | 0 | 0.033529 | Y | 61.7548 | 57.3398 | 7.149% | Y | 28.4047 | 29.6018 |  | 4544756.6023 | 378.7297 | 444027.4853 | 37.0023 | 341.7274 | Y |  |  | #REF!
Single | Double | Small | Hotel | PTAC | Electric |  | 33 | SingleDoubleSmallHotelPTACElectric33 | 0.33832 | 11.2244 | 0 | 0.033529 | Y | 53.3842 | 48.9692 | 8.27% | Y | 28.4047 | 54.6984 |  | 4544756.6023 | 378.7297 | 820476.5042 | 68.373 | 310.3567 | Y |  |  | #REF!
Single | Double | Small | Hotel | PTAC | Electric |  | 100 | SingleDoubleSmallHotelPTACElectric100 | 0.45927 | 13.6042 | 0 | 0.033529 | Y | 61.7548 | 57.3398 | 7.149% | Y | 28.4047 | 54.6984 |  | 4544756.6023 | 378.7297 | 820476.5042 | 68.373 | 310.3567 | Y |  |  | #REF!
Double | Single | Small | Hotel | PTAC | Electric |  | 33 | DoubleSingleSmallHotelPTACElectric33 | 0.23855 | 4.558 | 0 | 0.033529 | Y | 56.6258 | 52.2108 | 7.797% | Y | 26.5066 | 20.1219 |  | 4241050.1405 | 353.4208 | 301829.1336 | 25.1524 | 328.2684 | Y |  |  | #REF!
Double | Single | Small | Hotel | PTAC | Electric |  | 100 | DoubleSingleSmallHotelPTACElectric100 | 0.23945 | 5.6987 | 0 | 0.033529 | Y | 61.9924 | 57.5774 | 7.122% | Y | 26.5066 | 20.1219 |  | 4241050.1405 | 353.4208 | 301829.1336 | 25.1524 | 328.2684 | Y |  |  | 0.033529
Single | Single | Small | Hotel | PTHP | Electric | Low | 33 | SingleSingleSmallHotelPTHPElectricLow33 | 0.11905 | 6.0461 | 0 | 0.033529 | Y | 50.7112 | 46.2962 | 8.706% | Y | 28.4047 | 29.6018 |  | 4544756.6023 | 378.7297 | 444027.4853 | 37.0023 | 341.7274 | Y |  |  | 0.033529
Single | Single | Small | Hotel | PTHP | Electric | High | 33 | SingleSingleSmallHotelPTHPElectricHigh33 | 47.5036 | 6.0461 | 0 | 0.033529 | Y | 50.7112 | 46.2962 | 8.706% | Y | 28.4047 | 29.6018 |  | 4544756.6023 | 378.7297 | 444027.4853 | 37.0023 | 341.7274 | Y |  |  | 0.033529
Single | Single | Small | Hotel | PTHP | Electric | Low | 100 | SingleSingleSmallHotelPTHPElectricLow100 | 0.14734 | 7.2822 | 0 | 0.033529 | Y | 56.6865 | 52.2715 | 7.788% | Y | 28.4047 | 29.6018 |  | 4544756.6023 | 378.7297 | 444027.4853 | 37.0023 | 341.7274 | Y
Single | Single | Small | Hotel | PTHP | Electric | High | 100 | SingleSingleSmallHotelPTHPElectricHigh100 | 47.5333 | 7.2822 | 0 | 0.033529 | Y | 56.6865 | 52.2715 | 7.788% | Y | 28.4047 | 29.6018 |  | 4544756.6023 | 378.7297 | 444027.4853 | 37.0023 | 341.7274 | Y |  |  | 0.033529
Single | Double | Small | Hotel | PTHP | Electric | Low | 33 | SingleDoubleSmallHotelPTHPElectricLow33 | 0.15066 | 11.2244 | 0 | 0.033529 | Y | 50.7112 | 46.2962 | 8.706% | Y | 28.4047 | 54.6984 |  | 4544756.6023 | 378.7297 | 820476.5042 | 68.373 | 310.3567 | Y |  |  | 0.033529
Single | Double | Small | Hotel | PTHP | Electric | High | 33 | SingleDoubleSmallHotelPTHPElectricHigh33 | 47.4252 | 11.2244 | 0 | 0.033529 | Y | 50.7112 | 46.2962 | 8.706% | Y | 28.4047 | 54.6984 |  | 4544756.6023 | 378.7297 | 820476.5042 | 68.373 | 310.3567 | Y |  |  | 0.033529
Single | Double | Small | Hotel | PTHP | Electric | Low | 100 | SingleDoubleSmallHotelPTHPElectricLow100 | 0.19401 | 13.6042 | 0 | 0.033529 | Y | 56.6865 | 52.2715 | 7.788% | Y | 28.4047 | 54.6984 |  | 4544756.6023 | 378.7297 | 820476.5042 | 68.373 | 310.3567 | Y
Single | Double | Small | Hotel | PTHP | Electric | High | 100 | SingleDoubleSmallHotelPTHPElectricHigh100 | 47.8443 | 13.6042 | 0 | 0.033529 | Y | 56.6865 | 52.2715 | 7.788% | Y | 28.4047 | 54.6984 |  | 4544756.6023 | 378.7297 | 820476.5042 | 68.373 | 310.3567 | Y |  |  | 0.033529
Double | Single | Small | Hotel | PTHP | Electric | Low | 33 | DoubleSingleSmallHotelPTHPElectricLow33 | 0.10405 | 4.558 | 0 | 0.033529 | Y | 48.8359 | 44.4209 | 9.04% | Y | 26.5066 | 20.1219 |  | 4241050.1405 | 353.4208 | 301829.1336 | 25.1524 | 328.2684 | Y |  |  | 0.033529
Double | Single | Small | Hotel | PTHP | Electric | High | 33 | DoubleSingleSmallHotelPTHPElectricHigh33 | 23.4641 | 4.558 | 0 | 0.033529 | Y | 48.8359 | 44.4209 | 9.04% | Y | 26.5066 | 20.1219 |  | 4241050.1405 | 353.4208 | 301829.1336 | 25.1524 | 328.2684 | Y |  |  | 0.033529
Double | Single | Small | Hotel | PTHP | Electric | Low | 100 | DoubleSingleSmallHotelPTHPElectricLow100 | 0.099065 | 5.6987 | 0 | 0.033529 | Y | 55.8014 | 51.3864 | 7.912% | Y | 26.5066 | 20.1219 |  | 4241050.1405 | 353.4208 | 301829.1336 | 25.1524 | 328.2684 | Y
Double | Single | Small | Hotel | PTHP | Electric | High | 100 | DoubleSingleSmallHotelPTHPElectricHigh100 | 21.9388 | 5.6987 | 0 | 0.033529 | Y | 55.8014 | 51.3864 | 7.912% | Y | 26.5066 | 20.1219 |  | 4241050.1405 | 353.4208 | 301829.1336 | 25.1524 | 328.2684 | Y |  |  | 0.033529
Single | Single | Large | Hotel | FCU | Electric |  | 33 | SingleSingleLargeHotelFCUElectric33 | 0.065346 | 4.3186 | 0 |  | Y | 110.1377 | 105.7227 | 4.009% | Y | 37.0563 | 93.6999 |  | 5929009.9429 | 494.0842 | 1405498.6823 | 117.1249 | 376.9593 | Y |  |  | #REF!
Single | Single | Large | Hotel | FCU | Electric |  | 100 | SingleSingleLargeHotelFCUElectric100 | 0.10877 | 5.2016 | 0 |  | Y | 116.4981 | 112.0831 | 3.79% | Y | 37.0563 | 93.6999 |  | 5929009.9429 | 494.0842 | 1405498.6823 | 117.1249 | 376.9593 | Y |  |  | #REF!
Single | Double | Large | Hotel | FCU | Electric |  | 33 | SingleDoubleLargeHotelFCUElectric33 | 0.36073 | 8.0174 | 0 |  | Y | 110.1377 | 105.7227 | 4.009% | Y | 37.0563 | 186.7205 |  | 5929009.9429 | 494.0842 | 2800807.0289 | 233.4006 | 260.6836 | Y |  |  | #REF!
Single | Double | Large | Hotel | FCU | Electric |  | 100 | SingleDoubleLargeHotelFCUElectric100 | 0.54053 | 9.7173 | 0 |  | Y | 116.4981 | 112.0831 | 3.79% | Y | 37.0563 | 186.7205 |  | 5929009.9429 | 494.0842 | 2800807.0289 | 233.4006 | 260.6836 | Y |  |  | #REF!
Double | Single | Large | Hotel | FCU | Electric |  | 33 | DoubleSingleLargeHotelFCUElectric33 | 0.035928 | 3.2557 | 0 |  | Y | 103.0964 | 98.6814 | 4.282% | Y | 32.156 | 75.6363 |  | 5144956.4462 | 428.7464 | 1134543.8976 | 94.5453 | 334.201 | Y |  |  | #REF!
Double | Single | Large | Hotel | FCU | Electric |  | 100 | DoubleSingleLargeHotelFCUElectric100 | 0.077719 | 4.0705 | 0 |  | Y | 109.3794 | 104.9644 | 4.036% | Y | 32.156 | 75.6363 |  | 5144956.4462 | 428.7464 | 1134543.8976 | 94.5453 | 334.201 | Y |  |  | #REF!
Single | Single | Large | Hotel | FCU | Natural Gas |  | 33 | SingleSingleLargeHotelFCUNatural Gas33 | 0 | 4.3186 | 0.0038722 |  | Y | 111.2992 | 106.8842 | 3.967% | Y | 37.0563 | 93.6999 |  | 5929009.9429 | 494.0842 | 1405498.6823 | 117.1249 | 376.9593 | Y |  |  | #REF!
Single | Single | Large | Hotel | FCU | Natural Gas |  | 100 | SingleSingleLargeHotelFCUNatural Gas100 | 0 | 5.2016 | 0.0048633 |  | Y | 117.6789 | 113.2639 | 3.752% | Y | 37.0563 | 93.6999 |  | 5929009.9429 | 494.0842 | 1405498.6823 | 117.1249 | 376.9593 | Y |  |  | #REF!
Single | Double | Large | Hotel | FCU | Natural Gas |  | 33 | SingleDoubleLargeHotelFCUNatural Gas33 | 0 | 8.0174 | 0.0028885 |  | Y | 111.2992 | 106.8842 | 3.967% | Y | 37.0563 | 186.7205 |  | 5929009.9429 | 494.0842 | 2800807.0289 | 233.4006 | 260.6836 | Y |  |  | #REF!
Single | Double | Large | Hotel | FCU | Natural Gas |  | 100 | SingleDoubleLargeHotelFCUNatural Gas100 | 0 | 9.7173 | 0.0036631 |  | Y | 117.6789 | 113.2639 | 3.752% | Y | 37.0563 | 186.7205 |  | 5929009.9429 | 494.0842 | 2800807.0289 | 233.4006 | 260.6836 | Y |  |  | #REF!
Double | Single | Large | Hotel | FCU | Natural Gas |  | 33 | DoubleSingleLargeHotelFCUNatural Gas33 | 0 | 3.2557 | 0.0015323 |  | Y | 104.1237 | 99.7087 | 4.24% | Y | 32.156 | 75.6363 |  | 5144956.4462 | 428.7464 | 1134543.8976 | 94.5453 | 334.201 | Y |  |  | #REF!
Double | Single | Large | Hotel | FCU | Natural Gas |  | 100 | DoubleSingleLargeHotelFCUNatural Gas100 | 0 | 4.0705 | 0.0033663 |  | Y | 110.7392 | 106.3242 | 3.987% | Y | 32.156 | 75.6363 |  | 5144956.4462 | 428.7464 | 1134543.8976 | 94.5453 | 334.201 | Y |  |  | -1.5763
Single | Single |  | PS | FCU | Electric |  |  | SingleSinglePSFCUElectric | 11.4771 | 1.2037 | 0 |  | Y | 52.7062 | 49.3898 | 6.292% | Y | 29.217 | 26.9659 |  | 8765091.5863 | 730.4243 | 404488.7166 | 33.7074 | 696.7169 | Y |  |  | 0.68905
Single | Double |  | PS | FCU | Electric |  |  | SingleDoublePSFCUElectric | 10.5594 | 2.1225 | 0 |  | Y | 52.7062 | 49.3898 | 6.292% | Y | 29.0669 | 47.886 |  | 8720070.1218 | 726.6725 | 718289.5872 | 59.8575 | 666.815 | Y |  |  | 0.68905
Double | Single |  | PS | FCU | Electric |  |  | DoubleSinglePSFCUElectric | 5.9767 | 1.0194 | 0 |  | Y | 49.3542 | 46.0378 | 6.72% | Y | 26.3232 | 16.8093 |  | 7896949.1354 | 658.0791 | 252138.9164 | 21.0116 | 637.0675 | Y |  |  | 0.68905
Single | Single |  | PS | VAV | Electric |  |  | SingleSinglePSVAVElectric | 15.218 | 5.0873 | 0 |  | Y | 59.4106 | 56.0942 | 5.582% | Y | 29.217 | 26.9659 |  | 8765091.5863 | 730.4243 | 404488.7166 | 33.7074 | 696.7169 | Y |  |  | 0.32199
Single | Double |  | PS | VAV | Electric |  |  | SingleDoublePSVAVElectric | 15.0914 | 8.1155 | 0 |  | Y | 59.4106 | 56.0942 | 5.582% | Y | 29.0669 | 47.886 |  | 8720070.1218 | 726.6725 | 718289.5872 | 59.8575 | 666.815 | Y |  |  | 0.32199
Double | Single |  | PS | VAV | Electric |  |  | DoubleSinglePSVAVElectric | 11.031 | 4.1236 | 0 |  | Y | 54.822 | 51.5056 | 6.049% | Y | 26.3232 | 16.8093 |  | 7896949.1354 | 658.0791 | 252138.9164 | 21.0116 | 637.0675 | Y |  |  | 0.32199
Single | Single |  | PS | FCU | Natural Gas |  |  | SingleSinglePSFCUNatural Gas | 0 | 1.2037 | 0.4895 |  | Y | 56.9136 | 53.5972 | 5.827% | Y | 29.217 | 26.9659 |  | 8765091.5863 | 730.4243 | 404488.7166 | 33.7074 | 696.7169 | Y |  |  | 0.68905
Single | Double |  | PS | FCU | Natural Gas |  |  | SingleDoublePSFCUNatural Gas | 0 | 2.1225 | 0.45036 |  | Y | 56.9136 | 53.5972 | 5.827% | Y | 29.0669 | 47.886 |  | 8720070.1218 | 726.6725 | 718289.5872 | 59.8575 | 666.815 | Y |  |  | 0.68905
Double | Single |  | PS | FCU | Natural Gas |  |  | DoubleSinglePSFCUNatural Gas | 0 | 1.0194 | 0.25491 |  | Y | 52.7246 | 49.4081 | 6.29% | Y | 26.3232 | 16.8093 |  | 7896949.1354 | 658.0791 | 252138.9164 | 21.0116 | 637.0675 | Y |  |  | 0.68905
Single | Single |  | PS | VAV | Natural Gas |  |  | SingleSinglePSVAVNatural Gas | 0 | 5.0873 | 0.64905 |  | Y | 64.9834 | 61.6669 | 5.103% | Y | 29.217 | 26.9659 |  | 8765091.5863 | 730.4243 | 404488.7166 | 33.7074 | 696.7169 | Y |  |  | 0.32199
Single | Double |  | PS | VAV | Natural Gas |  |  | SingleDoublePSVAVNatural Gas | 0 | 8.1155 | 0.64365 |  | Y | 64.9834 | 61.6669 | 5.103% | Y | 29.0669 | 47.886 |  | 8720070.1218 | 726.6725 | 718289.5872 | 59.8575 | 666.815 | Y |  |  | 0.32199
Double | Single |  | PS | VAV | Natural Gas |  |  | DoubleSinglePSVAVNatural Gas | 0 | 4.1236 | 0.47047 |  | Y | 59.5943 | 56.2779 | 5.565% | Y | 26.3232 | 16.8093 |  | 7896949.1354 | 658.0791 | 252138.9164 | 21.0116 | 637.0675 | Y |  |  | 0.32199
Single | Single |  | SS | FCU | Electric |  |  | SingleSingleSSFCUElectric | 12.4996 | 1.2874 | 0 |  | Y | 74.5873 | 71.2709 | 4.446% | Y | 19.157 | 24.776 |  | 5747093.1089 | 478.9244 | 371639.4046 | 30.97 | 447.9545 | Y |  |  | 0.68905
Single | Double |  | SS | FCU | Electric |  |  | SingleDoubleSSFCUElectric | 11.5008 | 2.413 | 0 |  | Y | 74.5873 | 71.2709 | 4.446% | Y | 19.0129 | 45.7793 |  | 5703860.5029 | 475.3217 | 686689.1126 | 57.2241 | 418.0976 | Y |  |  | 0.68905
Double | Single |  | SS | FCU | Electric |  |  | DoubleSingleSSFCUElectric | 6.4473 | 1.0904 | 0 |  | Y | 70.2601 | 66.9437 | 4.72% | Y | 17.2576 | 15.6764 |  | 5177273.1197 | 431.4394 | 235146.1721 | 19.5955 | 411.8439 | Y |  |  | 0.68905
Single | Single |  | SS | VAV | Electric |  |  | SingleSingleSSVAVElectric | 16.9528 | 5.3603 | 0 |  | Y | 78.3585 | 75.042 | 4.232% | Y | 19.157 | 24.776 |  | 5747093.1089 | 478.9244 | 371639.4046 | 30.97 | 447.9545 | Y |  |  | 0.32199
Single | Double |  | SS | VAV | Electric |  |  | SingleDoubleSSVAVElectric | 15.6129 | 9.1059 | 0 |  | Y | 78.3585 | 75.042 | 4.232% | Y | 19.0129 | 45.7793 |  | 5703860.5029 | 475.3217 | 686689.1126 | 57.2241 | 418.0976 | Y |  |  | 0.32199
Double | Single |  | SS | VAV | Electric |  |  | DoubleSingleSSVAVElectric | 12.0936 | 4.3339 | 0 |  | Y | 73.7863 | 70.4699 | 4.495% | Y | 17.2576 | 15.6764 |  | 5177273.1197 | 431.4394 | 235146.1721 | 19.5955 | 411.8439 | Y |  |  | 0.32199
Single | Single |  | SS | FCU | Natural Gas |  |  | SingleSingleSSFCUNatural Gas | 0 | 1.2874 | 0.53311 |  | Y | 82.1113 | 78.7948 | 4.039% | Y | 19.157 | 24.776 |  | 5747093.1089 | 478.9244 | 371639.4046 | 30.97 | 447.9545 | Y |  |  | 0.68905
Single | Double |  | SS | FCU | Natural Gas |  |  | SingleDoubleSSFCUNatural Gas | 0 | 2.413 | 0.49051 |  | Y | 82.1113 | 78.7948 | 4.039% | Y | 19.0129 | 45.7793 |  | 5703860.5029 | 475.3217 | 686689.1126 | 57.2241 | 418.0976 | Y |  |  | 0.68905
Double | Single |  | SS | FCU | Natural Gas |  |  | DoubleSingleSSFCUNatural Gas | 0 | 1.0904 | 0.27498 |  | Y | 77.0938 | 73.7774 | 4.302% | Y | 17.2576 | 15.6764 |  | 5177273.1197 | 431.4394 | 235146.1721 | 19.5955 | 411.8439 | Y |  |  | 0.68905
Single | Single |  | SS | VAV | Natural Gas |  |  | SingleSingleSSVAVNatural Gas | 0 | 5.3603 | 0.72304 |  | Y | 87.1139 | 83.7975 | 3.807% | Y | 19.157 | 24.776 |  | 5747093.1089 | 478.9244 | 371639.4046 | 30.97 | 447.9545 | Y |  |  | 0.32199
Single | Double |  | SS | VAV | Natural Gas |  |  | SingleDoubleSSVAVNatural Gas | 0 | 9.1059 | 0.66589 |  | Y | 87.1139 | 83.7975 | 3.807% | Y | 19.0129 | 45.7793 |  | 5703860.5029 | 475.3217 | 686689.1126 | 57.2241 | 418.0976 | Y |  |  | 0.32199
Double | Single |  | SS | VAV | Natural Gas |  |  | DoubleSingleSSVAVNatural Gas | 0 | 4.3339 | 0.51537 |  | Y | 82.2746 | 78.9582 | 4.031% | Y | 17.2576 | 15.6764 |  | 5177273.1197 | 431.4394 | 235146.1721 | 19.5955 | 411.8439 | Y |  |  | 0.32199
Single | Single |  | Hosp | VAV | Electric |  |  | SingleSingleHospVAVElectric | 28.8332 | 12.3824 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 20.8647 | 14.063 |  | 4381577.776 | 365.1315 | 168756.2748 | 14.063 | 351.0685 | Y |  |  | 0.57542
Single | Double |  | Hosp | VAV | Electric |  |  | SingleDoubleHospVAVElectric | 34.0114 | 15.7058 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 20.8647 | 24.2892 |  | 4381577.776 | 365.1315 | 291470.6327 | 24.2892 | 340.8423 | Y |  |  | 0.57542
Double | Single |  | Hosp | VAV | Electric |  |  | DoubleSingleHospVAVElectric | 17.0499 | 6.9358 | 0 |  | Y | 204.4148 | 192.7624 | 5.7% | Y | 22.101 | 8.2079 |  | 4641216.1172 | 386.768 | 98494.6427 | 8.2079 | 378.5601 | Y |  |  | 0.57542
Single | Single |  | Hosp | VAV | Natural Gas |  |  | SingleSingleHospVAVNatural Gas | 0 | 12.3824 | 1.2603 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 20.8647 | 14.063 |  | 4381577.776 | 365.1315 | 168756.2748 | 14.063 | 351.0685 | Y |  |  | 0.57542
Single | Double |  | Hosp | VAV | Natural Gas |  |  | SingleDoubleHospVAVNatural Gas | 0 | 15.7058 | 1.5031 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 20.8647 | 24.2892 |  | 4381577.776 | 365.1315 | 291470.6327 | 24.2892 | 340.8423 | Y |  |  | 0.57542
Double | Single |  | Hosp | VAV | Natural Gas |  |  | DoubleSingleHospVAVNatural Gas | 0 | 6.9358 | 0.73653 |  | Y | 230.1992 | 218.5468 | 5.062% | Y | 22.101 | 8.2079 |  | 4641216.1172 | 386.768 | 98494.6427 | 8.2079 | 378.5601 | Y |  |  | 0.57542
Single | Single | Low | MF | PTAC | Electric |  |  | SingleSingleLowMFPTACElectric | 9.3268 | 5.4637 | 0 |  | Y | 44.472 | 31.852 | 28.38% | Y | 16.9578 | 31.7117 |  | 339155.7473 | 28.263 | 158558.3556 | 13.2132 | 15.0498 | Y | 0.80802 | 0.918 | 0.28907
Single | Double | Low | MF | PTAC | Electric |  |  | SingleDoubleLowMFPTACElectric | 6.8175 | 10.2374 | 0 |  | Y | 45.6137 | 32.9937 | 27.67% | Y | 16.9578 | 58.5049 |  | 339155.7473 | 28.263 | 292524.2514 | 24.377 | 3.886 | Y | 0.80802 | 0.918 | 0.28907
Double | Single | Low | MF | PTAC | Electric |  |  | DoubleSingleLowMFPTACElectric | 4.2241 | 3.9652 | 0 |  | Y | 42.4892 | 29.8692 | 29.7% | Y | 14.0724 | 21.5897 |  | 281448.2266 | 23.454 | 107948.4931 | 8.9957 | 14.4583 | Y | 0.80802 | 0.918 | 0.28907
Single | Single | Mid | MF | FCU | Electric |  |  | SingleSingleMidMFFCUElectric | 8.095 | 4.7229 | 0 |  | Y | 42.1565 | 29.5365 | 29.94% | Y | 14.1333 | 24.1347 |  | 282666.8789 | 23.5556 | 120673.729 | 10.0561 | 13.4994 | Y | 0.80802 | 0.918 | 0.55233
Single | Double | Mid | MF | FCU | Electric |  |  | SingleDoubleMidMFFCUElectric | 5.883 | 9.4893 | 0 |  | Y | 42.1565 | 29.5365 | 29.94% | Y | 14.1333 | 46.3741 |  | 282666.8789 | 23.5556 | 231870.5839 | 19.3225 | 4.233 | Y | 0.80802 | 0.918 | 0.55233
Double | Single | Mid | MF | FCU | Electric |  |  | DoubleSingleMidMFFCUElectric | 3.196 | 3.412 | 0 |  | Y | 39.3661 | 26.7461 | 32.06% | Y | 11.838 | 10.5346 |  | 236760.1721 | 19.73 | 52673.066 | 4.3894 | 15.3406 | Y | 0.80802 | 0.918 | 0.55233
Single | Single | Mid | MF | FCU | Natural Gas |  |  | SingleSingleMidMFFCUNatural Gas | 0 | 4.7229 | 0.34525 |  | Y | 44.492 | 31.872 | 28.36% | Y | 14.1333 | 24.1347 |  | 282666.8789 | 23.5556 | 120673.729 | 10.0561 | 13.4994 | Y | 0.80802 | 0.918 | 0.55233
Single | Double | Mid | MF | FCU | Natural Gas |  |  | SingleDoubleMidMFFCUNatural Gas | 0 | 9.4893 | 0.25091 |  | Y | 44.492 | 31.872 | 28.36% | Y | 14.1333 | 46.3741 |  | 282666.8789 | 23.5556 | 231870.5839 | 19.3225 | 4.233 | Y | 0.80802 | 0.918 | 0.55233
Double | Single | Mid | MF | FCU | Natural Gas |  |  | DoubleSingleMidMFFCUNatural Gas | 0 | 3.412 | 0.13631 |  | Y | 41.0992 | 28.4792 | 30.71% | Y | 11.838 | 10.5346 |  | 236760.1721 | 19.73 | 52673.066 | 4.3894 | 15.3406 | Y | 0.80802 | 0.918 | 0.55233
0
0

## Regresson List_Office
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions | Heating Savings Curve Comparisons
No. | Base | SGS Type | Office Size | HVAC/Fuel Type | Fuel Type | Hours | a | b | c | a | b | c |  | HDD | 1 v 10 |  | % delta
1 | Single | Single | Mid | PVAV_Elec | Electric | 2080 | 0.87047 | 0.001676 | -5.82e-08 | 2.4043 | 0.00056251 | -9.7e-09 |  | 0 | 0.87047 | 1.0451 | -20.06%
2 | Single | Single | Mid | PVAV_Elec | Electric | 2912 | 1.695 | 0.0023052 | -8.55e-08 | 3.7648 | 0.0011532 | -6.65e-08 |  | 1000 | 2.4883 | 2.7875 | -12.03%
3 | Single | Single | Mid | PVAV_Elec | Electric | 8760 | 16.0041 | 0.0025681 | -6.39e-08 | 6.1823 | 0.0040024 | -2.414e-07 |  | 2000 | 3.9896 | 4.4055 | -10.42%
4 | Single | Double | Mid | PVAV_Elec | Electric | 2080 | 1.2309 | 0.0012507 | -9.1e-09 | 4.2025 | 0.0010761 | -7.28e-08 |  | 3000 | 5.3746 | 5.8993 | -9.761%
5 | Single | Double | Mid | PVAV_Elec | Electric | 2912 | 1.9904 | 0.0018291 | -2.58e-08 | 5.4563 | 0.0024885 | -2.236e-07 |  | 4000 | 6.6432 | 7.2686 | -9.414%
6 | Single | Double | Mid | PVAV_Elec | Electric | 8760 | 19.7294 | 0.0019487 | -3.6e-08 | 7.4924 | 0.0055275 | -3.6e-07 |  | 5000 | 7.7954 | 8.5136 | -9.214%
7 | Double | Single | Mid | PVAV_Elec | Electric | 2080 | 0.36809 | 0.00078224 | -2.94e-08 | 1.2341 | 0.00086291 | -8.2844e-08 |  | 6000 | 8.8312 | 9.6343 | -9.094%
8 | Double | Single | Mid | PVAV_Elec | Electric | 2912 | 0.90209 | 0.00085224 | -1.84e-08 | 1.2423 | 0.0018367 | -1.7058e-07 |  | 7000 | 9.7506 | 10.6306 | -9.026%
9 | Double | Single | Mid | PVAV_Elec | Electric | 8760 | 10.3089 | 0.00060965 | -6.3e-09 | 1.6695 | 0.0033281 | -2.268e-07 |  | 8000 | 10.5536 | 11.5026 | -8.992%
10 | Single | Single | Large | VAV | Electric | 2080 | 1.0451 | 0.0018046 | -6.2176e-08 | 2.9952 | 0.00054436 | -1.1922e-08 |  | 9000 | 11.2401 | 12.2502 | -8.986%
11 | Single | Single | Large | VAV | Electric | 2912 | 1.9632 | 0.00248 | -8.4257e-08 | 4.691 | 0.0011371 | -6.8371e-08 |  | 10000 | 11.8103 | 12.8734 | -9.001%
12 | Single | Single | Large | VAV | Electric | 8760 | 17.8817 | 0.0027347 | -6.9507e-08 | 7.8631 | 0.0041845 | -2.5866e-07 |  | 11000 | 12.2641 | 13.3723 | -9.036%
13 | Single | Double | Large | VAV | Electric | 2080 | 1.4248 | 0.0013539 | -1.0265e-08 | 5.1829 | 0.0010799 | -8.2357e-08 |  | 12000 | 12.6015 | 13.7469 | -9.089%
14 | Single | Double | Large | VAV | Electric | 2912 | 2.3366 | 0.0019452 | -2.5309e-08 | 6.795 | 0.0025987 | -2.4798e-07
15 | Single | Double | Large | VAV | Electric | 8760 | 22.0222 | 0.0020809 | -4.0988e-08 | 9.5019 | 0.0059375 | -4.1904e-07 |  | HDD | 2 v 11 |  | % delta
16 | Double | Single | Large | VAV | Electric | 2080 | 0.4342 | 0.00085233 | -3.2055e-08 | 1.5494 | 0.00091568 | -9.2914e-08 |  | 0 | 1.695 | 1.9632 | -15.83%
17 | Double | Single | Large | VAV | Electric | 2912 | 1.0306 | 0.00093112 | -2.0723e-08 | 1.5594 | 0.0020586 | -2.0486e-07 |  | 1000 | 3.9147 | 4.3589 | -11.35%
18 | Double | Single | Large | VAV | Electric | 8760 | 11.4976 | 0.00062221 | -5.8971e-09 | 2.2115 | 0.0036711 | -2.6307e-07 |  | 2000 | 5.9633 | 6.5862 | -10.44%
19 | Single | Single | Mid | PVAV_Gas | Natural Gas | 2080 | 0.042695 | 8.1867e-05 | -2.8552e-09 | 2.4043 | 0.00056251 | -9.7e-09 |  | 3000 | 7.841 | 8.6449 | -10.25%
20 | Single | Single | Mid | PVAV_Gas | Natural Gas | 2912 | 0.083713 | 0.00011194 | -4.1327e-09 | 3.7648 | 0.0011532 | -6.65e-08 |  | 4000 | 9.5477 | 10.5351 | -10.34%
21 | Single | Single | Mid | PVAV_Gas | Natural Gas | 8760 | 0.78714 | 0.00012298 | -1.782e-07 | 6.1823 | 0.0040024 | -2.414e-07 |  | 5000 | 11.0834 | 12.2567 | -10.59%
22 | Single | Double | Mid | PVAV_Gas | Natural Gas | 2080 | 0.058867 | 6.1357e-05 | -4.908e-10 | 4.2025 | 0.0010761 | -7.28e-08 |  | 6000 | 12.448 | 13.8099 | -10.94%
23 | Single | Double | Mid | PVAV_Gas | Natural Gas | 2912 | 0.096359 | 8.942e-05 | -1.2781e-09 | 5.4563 | 0.0024885 | -2.236e-07 |  | 7000 | 13.6417 | 15.1946 | -11.38%
24 | Single | Double | Mid | PVAV_Gas | Natural Gas | 8760 | 0.95972 | 9.5436e-05 | -1.8077e-09 | 7.4924 | 0.0055275 | -3.6e-07 |  | 8000 | 14.6644 | 16.4107 | -11.91%
25 | Double | Single | Mid | PVAV_Gas | Natural Gas | 2080 | 0.017465 | 3.824e-05 | -1.454e-09 | 1.2341 | 0.00086291 | -8.2844e-08 |  | 9000 | 15.5161 | 17.4583 | -12.52%
26 | Double | Single | Mid | PVAV_Gas | Natural Gas | 2912 | 0.043295 | 4.1592e-05 | -9.041e-10 | 1.2423 | 0.0018367 | -1.7058e-07 |  | 10000 | 16.1967 | 18.3374 | -13.22%
27 | Double | Single | Mid | PVAV_Gas | Natural Gas | 8760 | 0.50115 | 2.9516e-05 | -2.97e-10 | 1.6695 | 0.0033281 | -2.268e-07 |  | 11000 | 16.7064 | 19.048 | -14.02%
28 | Single | Single | Large | VAV | Natural Gas | 2080 | 0.051034 | 8.7885e-05 | -3.0213e-09 | 2.9952 | 0.00054436 | -1.1922e-08 |  | 12000 | 17.0451 | 19.5901 | -14.93%
29 | Single | Single | Large | VAV | Natural Gas | 2912 | 0.09622 | 0.00012082 | -4.1033e-09 | 4.691 | 0.0011371 | -6.8371e-08
30 | Single | Single | Large | VAV | Natural Gas | 8760 | 0.87218 | 0.00013319 | -3.3867e-09 | 7.8631 | 0.0041845 | -2.5866e-07 |  | HDD | 3 v 12 |  | % delta
31 | Single | Double | Large | VAV | Natural Gas | 2080 | 0.068584 | 6.5753e-05 | -4.825e-10 | 5.1829 | 0.0010799 | -8.2357e-08 |  | 0 | 16.0041 | 17.8817 | -11.73%
32 | Single | Double | Large | VAV | Natural Gas | 2912 | 0.11084 | 9.4884e-05 | -1.2252e-09 | 6.795 | 0.0025987 | -2.4798e-07 |  | 1000 | 18.5083 | 20.5469 | -11.01%
33 | Single | Double | Large | VAV | Natural Gas | 8760 | 1.0746 | 0.00010117 | -2.0052e-09 | 9.5019 | 0.0059375 | -4.1904e-07 |  | 2000 | 20.8848 | 23.0731 | -10.48%
34 | Double | Single | Large | VAV | Natural Gas | 2080 | 0.021081 | 4.1282e-05 | -1.5477e-09 | 1.5494 | 0.00091568 | -9.2914e-08 |  | 3000 | 23.1334 | 25.4603 | -10.06%
35 | Double | Single | Large | VAV | Natural Gas | 2912 | 0.049487 | 4.5563e-05 | -1.0305e-09 | 1.5594 | 0.0020586 | -2.0486e-07 |  | 4000 | 25.2543 | 27.7085 | -9.718%
36 | Double | Single | Large | VAV | Natural Gas | 8760 | 0.5567 | 3.1069e-05 | -3.498e-10 | 2.2115 | 0.0036711 | -2.6307e-07 |  | 5000 | 27.2473 | 29.8176 | -9.433%
[14 empty] | 6000 | 29.1125 | 31.7878 | -9.189%
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2) | [6 empty] | 7000 | 30.85 | 33.6189 | -8.975%
[7 empty] | Baseline Cooling Load Coefficients |  |  | Cooling Coefficients |  |  |  | 8000 | 32.4596 | 35.311 | -8.784%
No. | Base | SGS Type | Office Size | HVAC System Type | Location |  | a | b | c | a | b | c |  | 9000 | 33.9415 | 36.8641 | -8.611%
1 | Single | Single | Mid |  |  |  | 19.7937 | 0.0034283 | -3.153e-07 | 21.1474 | 0.0060445 | -5.603e-07 |  | 10000 | 35.2955 | 38.2782 | -8.451%
2 | Single | Double | Mid |  |  |  | 19.7937 | 0.0034283 | -3.153e-07 | 45.4062 | 0.0096502 | -8.115e-07 |  | 11000 | 36.5218 | 39.5533 | -8.301%
3 | Double | Single | Mid |  |  |  | 17.8041 | 0.0027898 | -2.34e-07 | 15.6944 | 0.0034111 | -2.989e-07 |  | 12000 | 37.6202 | 40.6894 | -8.158%
4 | Single | Single | Large |  |  |  | 24.3073 | 0.0023954 | -2.005e-07 | 19.9673 | 0.0070543 | -7.612e-07
5 | Single | Double | Large |  |  |  | 24.3073 | 0.0023954 | -2.005e-07 | 46.0266 | 0.011787 | -1.1328e-06
6 | Double | Single | Large |  |  |  | 23.0197 | 0.0015842 | -7.35e-08 | 16.6364 | 0.0047085 | -5.485e-07
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Office Size | Fuel | Location | Hours | a | b | c
1 | Single | N/A | Mid | Electric | N/A | 2080 | 55.1811 | -0.002839 | 4.1e-07
2 | Single | N/A | Mid | Electric | N/A | 2912 | 69.3419 | -0.0051025 | 6.6e-07
3 | Single | N/A | Mid | Electric | N/A | 8760 | 155.2883 | -0.012402 | 1.42e-06
4 | Double | N/A | Mid | Electric | N/A | 2080 | 56.4687 | -0.0036288 | 3.8e-07
5 | Double | N/A | Mid | Electric | N/A | 2912 | 66.1222 | -0.0050973 | 6e-07
6 | Double | N/A | Mid | Electric | N/A | 8760 | 132.8104 | -0.007426 | 8.1e-07
7 | Single | N/A | Mid | Gas | N/A | 2080 | 59.3124 | -0.00244 | 4.1e-07
8 | Single | N/A | Mid | Gas | N/A | 2912 | 74.8824 | -0.0048032 | 1.115e-06
9 | Single | N/A | Mid | Gas | N/A | 8760 | 163.5203 | -0.0062067 | 9.8e-07
10 | Double | N/A | Mid | Gas | N/A | 2080 | 59.7013 | -0.0047265 | 4.7e-07
11 | Double | N/A | Mid | Gas | N/A | 2912 | 70.9425 | -0.0063586 | 6.5e-07
12 | Double | N/A | Mid | Gas | N/A | 8760 | 139.89 | -0.010483 | 1.14e-06
13 | Single | N/A | Large | Electric | N/A | 2080 | 58.2415 | -0.00473 | 7.1e-07
14 | Single | N/A | Large | Electric | N/A | 2912 | 90.2995 | -0.0075784 | 1.08e-06
15 | Single | N/A | Large | Electric | N/A | 8760 | 151.3971 | -0.0088017 | 1.21e-06
16 | Double | N/A | Large | Electric | N/A | 2080 | 59.5296 | 0.0058856 | 7.8e-07
17 | Double | N/A | Large | Electric | N/A | 2912 | 88.8428 | -0.0088189 | 1.16e-06
18 | Double | N/A | Large | Electric | N/A | 8760 | 143.1419 | -0.0096109 | 1.16e-06
19 | Single | N/A | Large | Gas | N/A | 2080 | 59.4612 | -0.0041882 | 6e-07
20 | Single | N/A | Large | Gas | N/A | 2912 | 93.5545 | -0.0066678 | 1.02e-06
21 | Single | N/A | Large | Gas | N/A | 8760 | 154.7148 | -0.0065439 | 1.04e-06
22 | Double | N/A | Large | Gas | N/A | 2080 | 61.096 | -0.0049 | 6.7e-07
23 | Double | N/A | Large | Gas | N/A | 2912 | 90.4449 | -0.0066078 | 9.2e-07
24 | Double | N/A | Large | Gas | N/A | 8760 | 151.3476 | -0.010117 | 1.22e-06
Cooling Adjustment Regressoins Regressions | [6 empty] | a | b | c | d
Mid-size Office | [6 empty] | 0.69722 | -0.00010782 | 3.6051e-08 | -6.4e-12
Large Office | [6 empty] | 0.7793 | 4.963e-05 | -2.8839e-08 | 1e-12

## Regresson List_SH
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Heating Coefficients (Part 2)
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Fuel Type | Occupancy | a | b | c | a | b | c
1 | Single | Single | Small | PTAC | Electric | 33 | 0.26195 | 0.0011672 | 7.07e-08 | 1.0416 | 0.0014359 | -7.425e-08
2 | Single | Single | Small | PTAC | Electric | 100 | 0.34628 | 0.0017406 | 3.3033e-08 | 1.9828 | 0.0013242 | -3.5574e-08
3 | Single | Double | Small | PTAC | Electric | 33 | 0.33832 | 0.00093325 | 8.5301e-08 | 2.4891 | 0.0025642 | -1.423e-07
4 | Single | Double | Small | PTAC | Electric | 100 | 0.45927 | 0.0014362 | 5.3247e-08 | 3.861 | 0.0026635 | -1.156e-07
5 | Double | Single | Small | PTAC | Electric | 33 | 0.23855 | 0.00024276 | 5.61e-08 | 0.77436 | 0.0011276 | -6.5352e-08
6 | Double | Single | Small | PTAC | Electric | 100 | 0.23945 | 0.00080163 | 1.4955e-08 | 0.96197 | 0.0013188 | -6.1448e-08
7 | Single | Single | Small | PTHP | Electric | 33 | 0.11905 | 0.00042364 | 4.7421e-08 | 1.0416 | 0.0014359 | -7.425e-08 | 47.5036 | -0.011031 | 7.4216e-07
8 | Single | Single | Small | PTHP | Electric | 100 | 0.14734 | 0.00065798 | 3.4171e-08 | 1.9828 | 0.0013242 | -3.5574e-08 | 47.5333 | -0.010875 | 7.3864e-07
9 | Single | Double | Small | PTHP | Electric | 33 | 0.15066 | 0.00032914 | 5.2461e-08 | 2.4891 | 0.0025642 | -1.423e-07 | 47.4252 | -0.011071 | 7.4204e-07
10 | Single | Double | Small | PTHP | Electric | 100 | 0.19401 | 0.0005347 | 4.1346e-08 | 3.861 | 0.0026635 | -1.156e-07 | 47.8443 | -0.011024 | 7.4493e-07
11 | Double | Single | Small | PTHP | Electric | 33 | 0.10405 | 7.4317e-05 | 3.079e-08 | 0.77436 | 0.0011276 | -6.5352e-08 | 23.4641 | -0.0055318 | 3.6817e-07
12 | Double | Single | Small | PTHP | Electric | 100 | 0.099065 | 0.00030373 | 1.5623e-08 | 0.96197 | 0.0013188 | -6.1448e-08 | 21.9388 | -0.0050138 | 3.4055e-07
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Base Peak Load Coefficient |  |  | Cooling Reduction Coefficients
No. | Base | SGS Type | Hotel Size | HVAC System Type | Location |  | a | b | c | a | b | c
1 | Single | Single | Small | N/A | N/A |  | 16.4825 | 0.0040935 | -3.244e-07 | 13.683 | 0.0061771 | -5.891e-07
2 | Single | Double | Small | N/A | N/A |  | 16.4825 | 0.0040935 | -3.244e-07 | 24.7902 | 0.011711 | -1.1299e-06
3 | Double | Single | Small | N/A | N/A |  | 16.2543 | 0.0040813 | -4.02e-07 | 8.6455 | 0.0043684 | -4.061e-07
EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Location | Occupancy | a | b | c
1 | Single | N/A | Small | PTAC | N/A | 33 | 53.3842 | -0.0018385 | 5.912e-07
3 | Single | N/A | Small | PTAC | N/A | 100 | 61.7548 | -0.0028943 | 6.6e-07
4 | Double | N/A | Small | PTAC | N/A | 33 | 56.6258 | -0.0021877 | 5.948e-07
6 | Double | N/A | Small | PTAC | N/A | 100 | 61.9924 | -0.0031041 | 6.701e-07
7 | Single | N/A | Small | PTHP | N/A | 33 | 50.7112 | -0.0053321 | 7.588e-07
9 | Single | N/A | Small | PTHP | N/A | 100 | 56.6865 | -0.0055582 | 7.785e-07
10 | Double | N/A | Small | PTHP | N/A | 33 | 48.8359 | -0.0046747 | 6.767e-07
12 | Double | N/A | Small | PTHP | N/A | 100 | 55.8014 | -0.0047838 | 6.515e-07
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.46864 | -0.00036016 | 1.0366e-07 | -1e-11

## Regresson List_LH
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2) except PTHP which is Exponential Curve
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | CSW Type | Hotel Size | HVAC/Fuel Type | Fuel Type | Occupancy | a | b | c | a | b | c
1 | Single | Single | Large |  | Electric | 33 | 0.065346 | 0.0010554 | 3.98e-08 | 0.74399 | 0.0010256 | -5.3036e-08
2 | Single | Single | Large |  | Electric | 100 | 0.10877 | 0.0016539 | 1.17e-08 | 1.4163 | 0.00094583 | -2.541e-08
3 | Single | Double | Large |  | Electric | 33 | 0.36073 | 0.00037113 | 9.16e-08 | 1.7779 | 0.0018316 | -1.0164e-07
4 | Single | Double | Large |  | Electric | 100 | 0.54053 | 0.0011271 | -8.46e-08 | 2.7579 | 0.0019025 | -8.2571e-08
5 | Double | Single | Large |  | Electric | 33 | 0.035928 | 0.00032251 | 2.38e-08 | 0.55312 | 0.00080546 | -4.668e-08
6 | Double | Single | Large |  | Electric | 100 | 0.077719 | 0.00051203 | 1.76e-08 | 0.68712 | 0.000942 | -4.3891e-08
7 | Single | Single | Large |  | Gas | 33 | 0.0038722 | 4.4682e-05 | 1.719e-09 | 0.74399 | 0.0010256 | -5.3036e-08
8 | Single | Single | Large |  | Gas | 100 | 0.0048633 | 7.0633e-05 | 4.82e-10 | 1.4163 | 0.00094583 | -2.541e-08
9 | Single | Double | Large |  | Gas | 33 | 0.0028885 | 1.7714e-05 | 3.57e-09 | 1.7779 | 0.0018316 | -1.0164e-07
10 | Single | Double | Large |  | Gas | 100 | 0.0036631 | 3.5852e-05 | 3.2519e-09 | 2.7579 | 0.0019025 | -8.2571e-08
11 | Double | Single | Large |  | Gas | 33 | 0.0015323 | 1.3755e-05 | 1.0151e-09 | 0.55312 | 0.00080546 | -4.668e-08
12 | Double | Single | Large |  | Gas | 100 | 0.0033663 | 2.1778e-05 | 7.593e-10 | 0.68712 | 0.000942 | -4.3891e-08
Peak Load Reduction Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Base Peak Load Coefficient |  |  | Cooling Reduction Coefficients
No. | Base | SGS Type | Hotel Size | HVAC System Type | Location |  | a | b | c | a | b | c
1 | Single | Single | Large | N/A | N/A |  | 22.9423 | 0.0049987 | -4.175e-07 | 51.0672 | 0.016653 | -1.6018e-06
2 | Single | Double | Large | N/A | N/A |  | 22.9423 | 0.0049987 | -4.175e-07 | 111.6874 | 0.029645 | -2.8927e-06
3 | Double | Single | Large |  |  |  | 21.1662 | 0.0033299 | -2.018e-07 | 44.687 | 0.011554 | -1.0455e-06
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type | Hotel Size | Fuel Type | Location | Occ | a | b | c
1 | Single | N/A | Large | Electric | N/A | 33 | 110.1377 | -0.0078283 | 9.88e-07
3 | Single | N/A | Large | Electric | N/A | 100 | 116.4981 | -0.0084816 | 1.0438e-06
4 | Double | N/A | Large | Electric | N/A | 33 | 103.0964 | -0.007085 | 8.928e-07
6 | Double | N/A | Large | Electric | N/A | 100 | 109.3794 | -0.0075483 | 9.197e-07
7 | Single | N/A | Large | Gas | N/A | 33 | 111.2992 | -0.0071869 | 1.0628e-06
9 | Single | N/A | Large | Gas | N/A | 100 | 117.6789 | -0.0078209 | 1.1174e-06
10 | Double | N/A | Large | Gas | N/A | 33 | 104.1237 | -0.0065781 | 9.638e-07
12 | Double | N/A | Large | Gas | N/A | 100 | 110.7392 | -0.0074406 | 1.0281e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.62037 | -0.0001621 | -5.1812e-08 | -4e-12

## Regresson List_PS
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions (change from red to black when coefficients are dialed in)
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | FCU | Elec | 0.053961 | 0.0021448 | -1.7946e-09 | 0.95809 | 0.00022102 | -1.2262e-09
2 | Single | Double |  | FCU | Elec | 0.13779 | 0.0019761 | -5.2529e-09 | 1.3489 | 0.00071388 | -1.9599e-08
3 | Double | Single |  | FCU | Elec | 0.0037853 | 0.0010767 | 7.4261e-09 | 0.81031 | 0.00018948 | -2.1621e-09
4 | Single | Single |  | VAV | Elec | 0.28479 | 0.0029384 | -2.75e-08 | 3.6664 | 0.0013575 | -7.74e-08
5 | Single | Double |  | VAV | Elec | 0.15624 | 0.0029248 | -2.49e-08 | 5.4819 | 0.0025477 | -1.718e-07
6 | Double | Single |  | VAV | Elec | 0.60465 | 0.0020275 | -1.47e-08 | 3.0243 | 0.001035 | -4.63e-08
7 | Single | Single |  | FCU | Gas | 0.0023014 | 9.1475e-05 | -7.65e-11 | 0.95809 | 0.00022102 | -1.2262e-09
8 | Single | Double |  | FCU | Gas | 0.0058768 | 8.4279e-05 | -2.24e-10 | 1.3489 | 0.00071388 | -1.9599e-08
9 | Double | Single |  | FCU | Gas | 0.00016144 | 4.5922e-05 | 3.167e-10 | 0.81031 | 0.00018948 | -2.1621e-09
10 | Single | Single |  | VAV | Gas | 0.012146 | 0.00012532 | -1.1729e-09 | 3.6664 | 0.0013575 | -7.74e-08
11 | Single | Double |  | VAV | Gas | 0.0066635 | 0.00012474 | -1.062e-09 | 5.4819 | 0.0025477 | -1.718e-07
12 | Double | Single |  | VAV | Gas | 0.025788 | 8.6472e-05 | -6.27e-10 | 3.0243 | 0.001035 | -4.63e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 23.1195 | 0.0061556 | -6.276e-07 | 21.1987 | 0.0056719 | -4.592e-07
2 | Single | VAV | Double | N/A |  | 23.0244 | 0.0060725 | -5.973e-07 | 40.881 | 0.0063162 | -4.52e-08
3 | Double | VAV | Single | N/A |  | 20.816 | 0.0054447 | -4.64e-07 | 13.1679 | 0.0036668 | -3.665e-07
4 | Single | FCU | Single | N/A |  | 23.1195 | 0.0061556 | -6.276e-07 | 21.1987 | 0.0056719 | -4.592e-07
5 | Single | FCU | Double | N/A |  | 23.0244 | 0.0060725 | -5.973e-07 | 40.881 | 0.0063162 | -4.52e-08
6 | Double | FCU | Single | N/A |  | 20.816 | 0.0054447 | -4.64e-07 | 13.1679 | 0.0036668 | -3.665e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 50.1109 | -0.0019976 | 6.983e-07
2 | Double | N/A |  | VAV | Elec | 48.2583 | -0.0023833 | 6.748e-07
3 | Single | N/A |  | VAV | Gas | 50.6134 | -0.0014571 | 7.744e-07
4 | Double | N/A |  | VAV | Gas | 48.767 | -0.0019935 | 7.509e-07
5 | Single | N/A |  | FCU | Elec | 34.7028 | 0.00039535 | 5.551e-07
6 | Double | N/A |  | FCU | Elec | 33.3119 | 0.00035673 | 4.938e-07
7 | Single | N/A |  | FCU | Gas | 36.0445 | 0.00018573 | 6.944e-07
8 | Double | N/A |  | FCU | Gas | 35.7159 | -0.00032935 | 6.558e-07

## Regresson List_SS
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions (change from red to black when coefficients are dialed in)
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | FCU | Elec | 0.07667 | 0.0023295 | -1.4e-09 | 1.0341 | 0.00022722 | -6e-10
2 | Single | Double |  | FCU | Elec | 0.16046 | 0.0021483 | -5.3467e-09 | 1.4756 | 0.00086338 | -2.23e-08
3 | Double | Single |  | FCU | Elec | 0.013688 | 0.001141 | 1.15e-08 | 0.87462 | 0.00019487 | -1.7e-09
4 | Single | Single |  | VAV | Elec | 0.30646 | 0.0032212 | -2.0506e-08 | 3.7648 | 0.001538 | -9.924e-08
5 | Single | Double |  | VAV | Elec | 0.26912 | 0.0030125 | -2.7017e-08 | 6.0997 | 0.0029145 | -2.0178e-07
6 | Double | Single |  | VAV | Elec | 0.60649 | 0.0021689 | -4.0728e-09 | 3.118 | 0.0011289 | -3.6959e-08
7 | Single | Single |  | FCU | Gas | 0.00327 | 9.9355e-05 | -5.97e-11 | 1.0341 | 0.00022722 | -6e-10
8 | Single | Double |  | FCU | Gas | 0.0068438 | 9.1624e-05 | -2.28e-10 | 1.4756 | 0.00086338 | -2.23e-08
9 | Double | Single |  | FCU | Gas | 0.0005838 | 4.8664e-05 | 4.905e-10 | 0.87462 | 0.00019487 | -1.7e-09
10 | Single | Single |  | VAV | Gas | 0.013071 | 0.00013738 | -8.746e-10 | 3.7648 | 0.001538 | -9.924e-08
11 | Single | Double |  | VAV | Gas | 0.011478 | 0.00012849 | -1.1523e-09 | 6.0997 | 0.0029145 | -2.0178e-07
12 | Double | Single |  | VAV | Gas | 0.030167 | 9.1132e-05 | -8.22e-11 | 3.118 | 0.0011289 | -3.6959e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 14.0663 | 0.0051478 | -5.317e-07 | 18.6274 | 0.0062097 | -6.352e-07
2 | Single | VAV | Double | N/A |  | 13.259 | 0.0058206 | -6.029e-07 | 37.7857 | 0.0078383 | -6.158e-07
3 | Double | VAV | Single | N/A |  | 12.3843 | 0.0049067 | -4.9e-07 | 12.5508 | 0.0030735 | -2.484e-07
4 | Single | FCU | Single | N/A |  | 14.0663 | 0.0051478 | -5.317e-07 | 18.6274 | 0.0062097 | -6.352e-07
5 | Single | FCU | Double | N/A |  | 13.259 | 0.0058206 | -6.029e-07 | 37.7857 | 0.0078383 | -6.158e-07
6 | Double | FCU | Single | N/A |  | 12.3843 | 0.0049067 | -4.9e-07 | 12.5508 | 0.0030735 | -2.484e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 53.562 | -0.0013443 | 1.1176e-06
2 | Double | N/A |  | VAV | Elec | 52.0153 | -0.0017659 | 1.0907e-06
3 | Single | N/A |  | VAV | Gas | 53.9476 | -0.00045128 | 1.2431e-06
4 | Double | N/A |  | VAV | Gas | 52.3491 | -0.00076439 | 1.1884e-06
5 | Single | N/A |  | FCU | Elec | 46.581 | -0.0009915 | 1.1638e-06
6 | Double | N/A |  | FCU | Elec | 45.9373 | -0.0016372 | 1.1558e-06
7 | Single | N/A |  | FCU | Gas | 47.0639 | -0.00053891 | 1.3252e-06
8 | Double | N/A |  | FCU | Gas | 46.471 | -0.0013285 | 1.3182e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
| VAV |  | 0.54363 | -0.0002672 | 6.9504e-08 | -7e-12
| FCU |  | 0.94835 | -0.00023927 | 5.443e-09 | 1e-12

## Regresson List_Hosp
Energy Savings Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c | a | b | c
1 | Single | Single |  | VAV | Elec | 19.2535 | 0.0021028 | -2.52e-08 | 8.3588 | 0.0051741 | -4.5098e-07 |  | -0.27284 | 0.0039845 | -2.1953e-07 | 1.5741 | 0.0081792 | -4.4986e-06
2 | Single | Double |  | VAV | Elec | 26.1154 | 0.0017024 | -1.44e-08 | 10.0933 | 0.0072545 | -6.7343e-07 |  | 0.074575 | 0.003999 | -2.8628e-07 | 0.78588 | 0.0092962 | -5.2852e-06
3 | Double | Single |  | VAV | Elec | 13.5118 | 0.00071769 | 2.8786e-09 | 3.6366 | 0.0042105 | -3.3164e-07 |  | 2.4796 | 0.0030728 | -1.6648e-07 | 1.6499 | 0.012552 | -6.349e-06
4 | Single | Single |  | VAV | Gas | 0.80257 | 9.1983e-05 | -1.2e-09 | 8.3588 | 0.0051741 | -4.5098e-07 |  | 2.2479 | 0.0021615 | -1.5232e-07 | 0.45658 | 0.017916 | -1.0135e-05
5 | Single | Double |  | VAV | Gas | 1.1203 | 7.3165e-05 | -3e-10 | 10.0933 | 0.0072545 | -6.7343e-07 |  | 0.02227 | 0.00015822 | -8.428e-09 | 1.2666 | 0.0088125 | -4.7465e-06
6 | Double | Single |  | VAV | Gas | 0.57628 | 3.0609e-05 | -1.228e-10 | 3.6366 | 0.0042105 | -3.3164e-07 |  | -1.0558 | 0.00047562 | -3.4052e-08 | 0.78682 | 0.0092579 | -5.1559e-06
[13 empty] | -0.19323 | 0.00021308 | -1.1548e-08 | 0.8344 | 0.016489 | -8.9439e-06
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2) | [6 empty] | -0.093324 | 0.00015414 | -1.1003e-08 | 0.45982 | 0.017847 | -9.932e-06
[6 empty] | Base Peak Load Coefficient |  |  | Cooling Coefficients
No. | Base | HVAC Type | CSW Type | Fuel |  | a | b | c | a | b | c
1 | Single | VAV | Single | N/A |  | 15.9452 | 0.0062549 | -4.666e-07 | 10.2212 | 0.004944 | -4.35e-07
2 | Single | VAV | Double | N/A |  | 15.9452 | 0.0062549 | -4.666e-07 | 16.1958 | 0.010505 | -1.0237e-06
3 | Double | VAV | Single | N/A |  | 19.62 | 0.003158 | -2.394e-07 | 5.1435 | 0.003977 | -3.869e-07
Baseline EUI Regressions | [5 empty] | Regression Form (a+bx+cx^2)
Coefficients
No. | Base | CSW Type |  | HVAC Type | Fuel | a | b | c
1 | Single | N/A |  | VAV | Elec | 222.3254 | -0.008719 | 1.229e-06
2 | Double | N/A |  | VAV | Elec | 217.221 | -0.0080141 | 1.1096e-06
3 | Single | N/A |  | VAV | Gas | 238.563 | -0.0081294 | 1.3234e-06
4 | Double | N/A |  | VAV | Gas | 229.9586 | -0.0063651 | 1.1099e-06
Cooling / Aux Split Regression |  |  | a | b | c | d
|  |  | 0.71341 | -0.00019542 | 3.9398e-08 | -3e-12

## Regresson List_MF
Energy Savings Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients |  |  | Notes/Assumptions
No. | Base | SGS Type | MF Type | HVAC/Fuel Type | Location | Occ | a | b | c | a | b | c
1 | Single | Single | Low | PTAC_Elec |  |  | 0.299 | 0.0025234 | 2.3682e-08 | 2.5605 | 0.0019479 | -6e-08
2 | Single | Double | Low | PTAC_Elec |  |  | 0.28229 | 0.0015466 | 9.7967e-08 | 4.7841 | 0.0037555 | -1.745e-07
3 | Double | Single | Low | PTAC_Elec |  |  | 0.10639 | 0.0011628 | 7.3912e-09 | 1.2302 | 0.0018858 | -8.9e-08
4 | Single | Single | Mid | FCU_Elec |  |  | 0.16121 | 0.0021418 | 4.2685e-08 | 2.4323 | 0.001554 | -5.8284e-08
5 | Single | Double | Mid | FCU_Elec |  |  | 0.14207 | 0.0012868 | 1.0679e-07 | 4.5673 | 0.0034876 | -2.2003e-07
6 | Double | Single | Mid | FCU_Elec |  |  | 0.058778 | 0.00076818 | 3.9601e-08 | 1.1837 | 0.0015549 | -8.4302e-08
7 | Single | Single | Mid | FCU_Gas |  |  | 0.0068754 | 9.1347e-05 | 1.8205e-09 | 2.4323 | 0.001554 | -5.8284e-08
8 | Single | Double | Mid | FCU_Gas |  |  | 0.0060592 | 5.4883e-05 | 4.5544e-09 | 4.5673 | 0.0034876 | -2.2003e-07
9 | Double | Single | Mid | FCU_Gas |  |  | 0.0025069 | 3.2763e-05 | 1.689e-09 | 1.1837 | 0.0015549 | -8.4302e-08
Peak Load Reduction Regressions | [5 empty] | Regression Form (a+bx+cx^2)
[6 empty] | Baseline Cooling Load Coefficients |  |  | Cooling Coefficients
No. | Base | MF Type | SGS Type | Fuel |  | a | b | c | a | b | c
1 | Single | Low | Single | N/A |  | 12.5835 | 0.0032441 | -2.879e-07 | 23.4622 | 0.0062223 | -6.095e-07
2 | Single | Low | Double | N/A |  | 12.5835 | 0.0032441 | -2.879e-07 | 50.0156 | 0.0060901 | -4.273e-07
3 | Double | Low | Single | N/A |  | 10.599 | 0.0025959 | -2.413e-07 | 18.2796 | 0.0021591 | -2.9e-08
4 | Single | Mid | Single | N/A |  | 10.3001 | 0.0027499 | -1.929e-07 | 16.6972 | 0.0055256 | -4.957e-07
5 | Single | Mid | Double | N/A |  | 10.3001 | 0.0027499 | -1.929e-07 | 34.8294 | 0.0084273 | -6.738e-07
6 | Double | Mid | Single | N/A |  | 8.7783 | 0.0021889 | -1.501e-07 | 11.1553 | 0 | -2.531e-07
Baseline EUI Regressions | [6 empty] | Regression Form (a+bx+cx^2)
[7 empty] | Heating Coefficients |  |  | Cooling Coefficients
No. | Base | SGS Type | MF Type | HVAC Type | Fuel |  | a | b | c | a | b | c
1 | Single | N/A | Low | PTAC | Elec |  | 50.1496 | -0.0039338 | 6.624e-07 | 50.1496 | -0.0039338 | 6.624e-07
2 | Double | N/A | Low | PTAC | Elec |  | 42.4892 | -0.002642 | 5.102e-07 | 42.4892 | -0.002642 | 5.102e-07
3 | Single | N/A | Mid | FCU | Elec |  | 47.6672 | -0.0038797 | 6.607e-07 | 47.6672 | -0.0038797 | 6.607e-07
4 | Double | N/A | Mid | FCU | Elec |  | 44.8676 | -0.0035527 | 5.671e-07 | 44.8676 | -0.0035527 | 5.671e-07
5 | Single | N/A | Mid | FCU | Gas |  | 47.7768 | -0.0034438 | 7.203e-07 | 47.7768 | -0.0034438 | 7.203e-07
6 | Double | N/A | Mid | FCU | Gas |  | 44.9531 | -0.0032699 | 6.227e-07 | 44.9531 | -0.0032699 | 6.227e-07
Savings Adjustment Factor Regressions
No. | Base | CSW Type | Single | HVAC | Fuel |  | a | b | c | d
1 | Single | Single | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
2 | Single | Double | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
3 | Double | Single | Low | PTAC | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
4 | Single | Single | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
5 | Single | Double | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
6 | Double | Single | Mid | FCU | Elec |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
7 | Single | Single | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
8 | Single | Double | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
9 | Double | Single | Mid | FCU | Gas |  | 0.86043 | -2.2759e-05 | 2.5496e-09 | -1e-13
Savings Adjustment Factor Regressions (Cool)
No. | Base | CSW Type | MF Type | HVAC | Fuel |  | a | b | c | d
1 | Single | Single | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
2 | Single | Double | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
3 | Double | Single | Low | PTAC | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
4 | Single | Single | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
5 | Single | Double | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
6 | Double | Single | Mid | FCU | Elec |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
7 | Single | Single | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
8 | Single | Double | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
9 | Double | Single | Mid | FCU | Gas |  | 0.96487 | -4.3579e-05 | 1.028e-08 | -1e-12
Cooling Adjustment Regressoins Regressions | [6 empty] | a | b | c | d
Mid-size | [6 empty] | 0.86172 | -0.00029049 | 7.5e-08 | -1e-11
Low-rise | [6 empty] | 0.64499 | -0.00035283 | 9.583e-08 | -1e-11

## Lists
Type of Glass | State | Alabama | Alaska | Arizona | Arkansas | California | Colorado | Connecticut | Delaware | Florida | Georgia | Hawaii | Idaho | Illinois | Indiana | Iowa | Kansas | Kentucky | Louisiana | Maine | Maryland | Massachusetts | Michigan | Minnesota | Mississippi | Missouri | Montana | Nebraska | Nevada | New_Hampshire | New_Jersey | New_Mexico | New_York | North_Carolina | North_Dakota | Ohio | Oklahoma | Oregon | Pennsylvania | Rhode_Island | South_Carolina | South_Dakota | Tennessee | Texas | Utah | Vermont | Virginia | Washington | West_Virginia | Wisconsin | Wyoming | Dist._of_Columbia | SGS Type | Fuel | HVAC Type, Office | Building Type | Occ | Infil | Cooling
Single pane | Alabama | Anniston | Adak | Casa Granda | Batesville | Alturas | Akron CO | Danbury | Dover | Crestview | Albany GA | Hilo | Boise | Aurora IL | Bloomington IN | Algona | Chanute | Bowling Green | Alexandria LA | Auburn ME | Baltimore | Beverly | Alpena | Aitkin | Biloxi | Cape Girardeau | Billings | Ainsworth | Elko | Berlin | Atlantic City | Alamogordo | Albany NY | Asheville | Bismarck | Akron OH | Altus | Astoria | Allentown | New Shoreham | Anderson | Aberdeen SD | Blountville | Abilene | Blanding | Burlington VT | Abingdon | Aberdeen WA | Beckley | Antigo | Casper | Washington DC | Single | Electric | Packaged VAV with electric reheat | Office | 33% | Included | Yes
Double pane | Alaska | Auburn AL | Anchorage | Douglas | Bentonville | Bakersfield | Alamosa | Groton | Wilmington DE | Daytona | Alma | Honolulu | Burley | Belleville | Evansville | Atlantic | Concordia | Fort Knox | Baton Rouge | Augusta ME | Camp Springs | Boston | Ann Arbor | Albert Lea | Columbus MS | Columbia MO | Bozeman | Alliance | Ely | Concord NH | Belmar | Albuquerque | Binghamton | Cape Hatteras | Devils Lake | Cincinnati | Bartlesville | Aurora OR | Altoona | Pawtucket | Beaufort | Brookings | Chattanooga | Alice | Bryce Canyon City | Montpelier | Blacksburg | Bellingham | Bluefield | Appleton | Cheyenne |  | Double | Natural Gas | Packaged VAV with hydronic reheat | Hotel | 66% | Excluded | No
New double pane (U<0.35) | Arizona | Birmingham | Aniak | Flagstaff | El Dorado | Bishop | Aspen | Hartford Brainard |  | Fort Lauderdale | Athens | Kahului | Caldwell | Bloomington IL | Fort Wayne | Boone | Dodge City | Hebron | Bossier City | Bangor | Hagerstown | Chicopee Falls | Battle Creek | Alexandria MN | Greenville MS | Farmington MO | Butte | Beatrice | Fallon | Keene | Fairfield NJ | Carlsbad NM | Buffalo | Charlotte | Dickinson | Cleveland | Clinton OK | Baker City | Bradford | Providence | Charleston SC | Huron | Crossville | Amarillo | Cedar City | Rutland | Charlottesville | Bremerton | Bridgeport | Eau Claire | Cody |  |  | None | Built-up VAV with hydronic reheat | Primary School | 100%
| Arkansas | Daleville | Annette Island | Grand Canyon | Fayetteville AR | Blue Canyon | Aurora CO | New Haven |  | Fort Myers | Atlanta | Kalaoa | Coeur d'Alene | Bondville | Huntingburg | Burlington IA | Emporia | Henderson City | Houma | Bar Harbor | Lexington Park | Hyannis | Benton Harbor | Austin MN | Greenwood | Ft. Leonard Wood | Cut Bank | Bellevue | Las Vegas NV | Laconia | Millville | Clayton | Elmira | Elizabeth City | Fargo | Columbus OH | Enid | Burns | Butler |  | Columbia SC | Mitchell | Dyersburg | Austin TX | Delta | Springfield VT | Danville | Ephrata | Charleston WV | Green Bay | Evanston |  |  |  | Other | Secondary School
| California | Dothan | Anvik | Kingman | Flippin | Blythe | Broomfield | Oxford |  | Fort Pierce | Augusta GA | Kaneohe | Grand View | Chicago | Indianapolis | Carroll | Garden City | Hopkinsville | Lafayette LA | Brunswick ME | Salisbury | Lawrence | Cadillac | Baudette | Gulfport | Jefferson City | Glasgow | Broken Bow | Lovelock | Lebanon | Newark | Clovis | Glen Falls | Fayetteville NC | Grand Forks | Dayton | Fort Sill | Corvallus | DuBois |  | Florence | Mobridge | Jackson TN | Brownsville | Hanksville |  | Farmville | Everett | Elkins | Janesville | Gillette |  |  | Electric Only |  | Hospital
| Colorado | Gadsen | Big River Lakes | Luke | Fort Smith | Burbank | Colorado Springs | Stratford |  | Gainesville | Brunswick GA | Kapalua | Hailey | Decatur | Kokomo | Cedar Rapids | Goodland | Jackson KY | Lake Charles | Caribou |  | Marthas Vineyard | Calumet | Bemidji | Hattiesburg | Joplin | Glendive | Chadron | Mercury | Manchester | Rio Grande | Deming | Jamestown NY | Goldsboro | Jamestown ND | Findlay | Gage | Eugene | Erie |  | Greenville SC | Pierre | Knoxville TN | Childress | Moab |  | Franklin VA | Forks | Huntington | La Cross | Jackson Hole |  |  | Electric | HVAC Type, Hotel | Multi-family
| Connecticut | Huntsville | Birchwood | Page | Harrison | Camarillo | Cortez |  |  | Homestead | Columbus GA | Kapolei | Idaho Falls | Marion IL | Lafayette IN | Chariton | Great Bend | Lexington | Leesville | Frenchville |  | Mashpee | Detroit | Benson | Jackson MS | Kaiser | Great Falls | Columbus NE | Reno | Mount Washington | Teterboro | Farmington NM | Massena | Greensboro | Minot | Mansfield | Hobart | Klamath Falls | Franklin PA |  | Greer | Rapid City | Memphis | College Station | Ogden |  | Fredericksburg | Hanford | Lewisburg | Lone Rock | Lander |  |  | None | PTAC | Other
| Delaware | Mobile | Chulitna | Phoenix | Hot Springs AR | Camp Pendleton | Craig |  |  | Jacksonville FL | Macon | Kapolei | Lewiston | Moline | Muncie | Charles City | Hays | London | Monroe | Houlton |  | Nantucket | Escanaba | Brainerd | McComb | Kansas City | Havre | Falls City | Tonopah | Portsmouth | Trenton | Gallup | Monticello NY | Greenville NC | Williston | Toledo OH | Lawton | La Grande | Harrisburg |  | Myrtle Beach | Sioux Falls | Nashville | Corpus Christi | Provo |  | Hampton | Hoquiam | Martinsburg | Madison | Laramie |  |  |  | PTHP
| Dist._of_Columbia | Montgomery | Cold Bay | Prescott | Jonesboro | Carlsbad CA | Denver |  |  | Key West | Marietta | Lanai | Malad City | Mount Vernon | South Bend | Clarinda | Hill City | Louisville | New Iberia | Millinocket |  | New Bedford | Flint | Cambridge | Meridian | Kirksville | Helena | Fremont | Winnemucca |  |  | Las Cruces | New Windsor | Havelock |  | Youngstown | McAlester | Lakeview | Johnstown |  | North Myrtle Beach | Watertown SD |  | Cotulla | Saint George |  | Hillsville | Kelso | Morgantown | Manitowac | Rawlins |  |  |  | Fan Coil Unit
| Florida | Muscle Shoals | Cordova | Safford | Little Rock | Chino | Durango |  |  | Lakeland | Rome | Lihue | Pocatello | Murphysboro | Terre Haute | Clinton IA | Hutchinson KS | Somerset | New Orleans | Portland ME |  | North Adams | Freeland | Cloquet | Natchez | Poplar Bluff | Kalispell | Grand Island |  |  |  | Las Vegas NM | New York | Hickory |  | Zanesville | Oklahoma City | Medford | Lancaster PA |  | Sumter | Yankton |  | Dalhart | Salt Lake City |  | Hot Springs VA | Moses Lake | parkersburg | Marshfield | Riverton |  |  |  | Other
| Georgia | Troy | Dillingham | Scottsdale | Pine Bluff | Chula Vista | Fort Collins |  |  | Marathon | Savannah | Molokai | Salmon | Peoria |  | Council Bluffs | Junction City | West Paducah | Patterson | Presque Isle |  | Norwood | Grand Rapids MI | Crane Lake | Starkville | Springfield MO | Lewistown | Hastings |  |  |  | Roswell | Nigara Falls | Jacksonville NC |  |  | Ponca City | North Bend | Middletown |  |  |  |  | Dallas | Vernal |  | Leesburg | Olympia | Wheeling | Milwaukee | Rock Springs
| Hawaii | Tuscaloosa | Dutch Harbor | Show Low | Rogers | Concord CA | Grand Junction |  |  | Mayport | Valdosta |  | Soda Springs | Quincy |  | Creston | Liberal |  | Pineville | Rockland |  | Plymouth | Houghton Lake | Crookston | Tupelo | St. Joseph | Livingston | Holdrege |  |  |  | Ruidoso | Republic | Kinston |  |  | Stillwater | Pendleton | Philadelphia |  |  |  |  | Del Rio | Wendover |  | Lynchburg | Pasco |  | Minocqua | Sheridan |  |  |  | HVAC Type, School
| Idaho |  | Emmonak | Tucson | Siloam Spring | Crescent City | Greeley |  |  | Melbourne | Warner Robins |  | Twin Falls | Rock Falls |  | Decorah | Manhattan |  | Shreveport | Sanford |  | Provincetown | Howell | Detroit Lakes |  | St. Louis | Miles City | Imperial NE |  |  |  | Santa Fe | Rockester | Manteo |  |  | Tulsa | Portland OR | Pittsburgh |  |  |  |  | El Paso |  |  | Manassas | Port Angeles |  | Mosinee | Workland |  |  |  | Central Ducted VAV
| Illinois |  | Fairbanks | Winslow | Springdale | Daggett | Gunnison |  |  | Miami |  |  |  | Rockford |  | Denison | Newton KS |  |  | Waterville |  | Westfield | Ironwood | Duluth |  | Vichy | Missoula | Kearney |  |  |  | Taos | Ronkonkoma | New Bern |  |  |  | Redmond | Reading |  |  |  |  | Galveston |  |  | Marion VA | Pullman |  | Oshkosh |  |  |  |  | Fan Coil Unit
| Indiana |  | Gustavus | Yuma | Stuttgart | Fairfield CA | Gypsum |  |  | Milton |  |  |  | Springfield IL |  | Des Moines | Olathe |  |  | Wiscasset |  | Worchester | Jackson MI | Ely |  | Warrensburg | Sidney MT | Lincoln |  |  |  | Truth or Consequences | Saranac Lake | Raleigh |  |  |  | Roseburg | Scranton |  |  |  |  | Georgetown |  |  | Martinsville | Renton |  | Phillips |  |  |  |  | Other
| Iowa |  | Healy |  | Texarkana | Fresno | Hayden |  |  | Naples |  |  |  | West Chicago |  | Dubuque | Russell | [5 empty] | Kalamazoo | Eveleth |  |  | Wolf Point | McCook |  |  |  | Tucumcari | Syracuse | Rocky Mount |  |  |  | Salem | University Park |  |  |  |  | Greenville TX |  |  | Melfa | Seattle |  | Rhinelander
| Kansas |  | Homer |  | Walnut Ridge | Fullerton | La Junta |  |  | Ocala | [5 empty] | Estherville | Salina | [5 empty] | Kincheloe | Fairmont |  |  |  | Norfolk NE |  |  |  |  | Utica | Southern Pines |  |  |  | Sexton Summit | Washington PA |  |  |  |  | Harlingen |  |  | Newport News | Spokane |  | Rice Lake |  |  |  |  | Packaged VAV with electric reheat | PVAV_Elec
| Kentucky |  | Hoonah |  |  | Hawthorne | Lakewood |  |  | Orlando | [5 empty] | Fairfield IA | Topeka | [5 empty] | Kingsford | Faribault |  |  |  | North Platte |  |  |  |  | Wappingers Falls | Wilmington NC |  |  |  |  | Williamsport |  |  |  |  | Hondo |  |  | Norfolk VA | Stampede Pass |  | Sturgeon Bay |  |  |  |  | Packaged VAV with hydronic reheat | PVAV
| Louisiana |  | Hooper Bay |  |  | Hayward | Lamar |  |  | Panama City | [5 empty] | Fort Dodge | Wichita | [5 empty] | Lansing | Fergus Falls |  |  |  | Omaha |  |  |  |  | Watertown NY | Winston-Salem | [9 empty] | Houston |  |  | Petersburg VA | Tacoma |  | Watertown WI |  |  |  |  | Built-up VAV with hydronic reheat | VAV
| Maine |  | Huslia |  |  | Imperial CA | Leadville |  |  | Pensacola | [5 empty] | Fort Madison | [6 empty] | Manistee | Flying Cloud |  |  |  | O'Neill |  |  |  |  | Westhampton Beach | [10 empty] | Killeen |  |  | Pulaski | The Dalles |  | Wausau |  |  |  |  | Central Ducted VAV | VAV
| Maryland |  | Iliamna |  |  | Lancaster CA | Limon |  |  | Sarasota | [5 empty] | Keokuk | [6 empty] | Marie | Fosston |  |  |  | Ord |  |  |  |  | White Plains | [10 empty] | Kingsville |  |  | Quantico | Toledo WA | [6 empty] | PTAC | PTAC
| Massachusetts |  | Juneau |  |  | Lemoore | Montrose |  |  | St. Petersburg | [5 empty] | Knoxville IA | [6 empty] | Menominee | Glenwood |  |  |  | Scottsbluff | [15 empty] | Laredo |  |  | Richmond | Walla Walla | [6 empty] | PTHP | PTHP
| Michigan |  | Kake |  |  | Livermore | Pueblo |  |  | Tallahasse | [5 empty] | Le Mars | [6 empty] | Mount Clemens | Grand Rapids MN |  |  |  | Sidney NE | [15 empty] | Longview |  |  | Roanoke | Wenatchee | [6 empty] | Fan Coil Unit | FCU
| Minnesota |  | Kenai |  |  | Lompoc | Rifle |  |  | Tampa | [5 empty] | Mason City | [6 empty] | Muskegon | Hallock |  |  |  | Tekamah | [15 empty] | Lubbock |  |  | Virginia Beach | Whidbey Island | [6 empty] | Other | FCU
| Mississippi |  | Ketchikan |  |  | Long Beach | Trinidad |  |  | Vero Beach | [5 empty] | Monticello IA | [6 empty] | Oscoda | Hibbing |  |  |  | Valentine | [15 empty] | Lufkin |  |  | Weyers Cave | Yakima
| Missouri |  | King Salmon |  |  | Los Angeles |  |  |  | West Palm Beach | [5 empty] | Muscatine | [6 empty] | Pellston | Hutchinson | [19 empty] | Marfa |  |  | Winchester
| Montana |  | Kodiak |  |  | McKinleyville | [9 empty] | Newton IA | [6 empty] | Port Huron | International Falls | [19 empty] | McAllen |  |  | Wise | [7 empty] | HVAC Type, Hospital
| Nebraska |  | Mekoryuk |  |  | Merced | [9 empty] | Oelwen | [6 empty] | Traverse City | Litchfield | [19 empty] | McGregor | [10 empty] | Central Ducted VAV | VAV
| Nevada |  | Middleton Island |  |  | Modesto | [9 empty] | Orange City | [6 empty] | Waterford Township | Little Falls | [19 empty] | Midland | [10 empty] | Other | VAV
| New_Hampshire |  | Palmer |  |  | Montague | [9 empty] | Ottumwa | [7 empty] | Mankato | [19 empty] | Mineral wells
| New_Jersey |  | Petersburg AK |  |  | Monterey | [9 empty] | Red Oak | [7 empty] | Marshall | [19 empty] | Nacogdockes | [10 empty] | HVAC Type, Mid-rise Multi-family
| New_Mexico |  | Point Heiden |  |  | Napa | [9 empty] | Sheldon | [7 empty] | Minneapolis | [19 empty] | Palacios | [10 empty] | Fan Coil Unit
| New_York |  | Saint Mary's |  |  | Needles | [9 empty] | Shenandoah | [7 empty] | Mora | [19 empty] | Paris | [10 empty] | Other
| North_Carolina |  | Sand Point |  |  | Oakland | [9 empty] | Sioux City | [7 empty] | Morris | [19 empty] | Port Arthur
| North_Dakota |  | Seward |  |  | Oxnard | [9 empty] | Spencer | [7 empty] | New Ulm | [19 empty] | Rockport | [10 empty] | HVAC Type, Low-rise Multi-family
| Ohio |  | Sitka Japonski |  |  | Palm Springs | [9 empty] | Storm Lake | [7 empty] | Orr | [19 empty] | San Angelo | [10 empty] | PTAC
| Oklahoma |  | Skagway |  |  | Palmdale | [9 empty] | Washington IA | [7 empty] | Owatonna | [19 empty] | San Antonio | [10 empty] | Other
| Oregon |  | Soldotna |  |  | Paso Robles | [9 empty] | Waterloo | [7 empty] | Park Rapids | [19 empty] | Temple
| Pennsylvania |  | St. Paul |  |  | Porterville | [9 empty] | Webster City | [7 empty] | Pipestone | [19 empty] | Tyler
| Rhode_Island |  | Talkeetna |  |  | Red Bluff | [17 empty] | Red Wing | [19 empty] | Victoria
| South_Carolina |  | Togiac |  |  | Redding | [17 empty] | Redwood Falls | [19 empty] | Waco
| South_Dakota |  | Utqiagvik |  |  | Ridgecrest | [17 empty] | Rochester | [19 empty] | Wichita Falls
| Tennessee |  | Valdez |  |  | Riverside | [17 empty] | Roseau | [19 empty] | Wink
| Texas |  | Whittier |  |  | Sacremento | [17 empty] | Silver Bay
| Utah |  | Wrangell |  |  | Salinas | [17 empty] | St Cloud
| Vermont |  | Yakutat |  |  | San Diego | [17 empty] | St Paul
| Virginia |  |  |  |  | San Francisco | [17 empty] | Thief River Falls
| Washington |  |  |  |  | San Jose | [17 empty] | Two Harbors
| West_Virginia |  |  |  |  | San Luis Obispo | [17 empty] | Wheaton
| Wisconsin |  |  |  |  | Sandberg | [17 empty] | Willmar
| Wyoming |  |  |  |  | Santa Anna | [17 empty] | Winona
[6 empty] | Santa Barbara | [17 empty] | Worthington
Santa Maria
Santa Monica
Santa Rose
South Lake Tahoe
Stockton
Truckee
Twentynine Palms
Ukiah
Van Nuys
Visalia
Yuba City

## Weather Information
State | Cities | Heating Degree Days (HDD) | Cooling Degree Days (CDD)
Alabama | Anniston | 2585 | 1713 |  | State | City | HDD | CDD | State | City | HDD | CDD | State | City | HDD | CDD
Alabama | Auburn AL | 2688 | 1477 |  | Alabama | Anniston | 2585 | 1713 | Arkansas | Batesville | 3761 | 1687 |  | Stockton | 2494 | 1296
Alabama | Birmingham | 2698 | 1912 |  |  | Auburn AL | 2688 | 1477 |  | Bentonville | 4394 | 1514 |  | Truckee | 7884 | 87
Alabama | Daleville | 2447 | 2122 |  |  | Birmingham | 2698 | 1912 |  | El Dorado | 2672 | 2512 |  | Twentynine Palms | 1788 | 3297
Alabama | Dothan | 2072 | 2443 |  |  | Daleville | 2447 | 2122 |  | Fayetteville AR | 3726 | 1753 |  | Ukiah | 2981 | 874
Alabama | Gadsen | 3063 | 1383 |  |  | Dothan | 2072 | 2443 |  | Flippin | 3724 | 1604 |  | Van Nuys | 1214 | 1507
Alabama | Huntsville | 3472 | 1701 |  |  | Gadsen | 3063 | 1383 |  | Fort Smith | 3596 | 2020 |  | Visalia | 3032 | 1602
Alabama | Mobile | 1724 | 2524 |  |  | Huntsville | 3472 | 1701 |  | Harrison | 3822 | 1590 |  | Yuba City | 2533 | 1476
Alabama | Montgomery | 2183 | 2124 |  |  | Mobile | 1724 | 2524 |  | Hot Springs AR | 3256 | 2111 | Colorado | Akron CO | 6087 | 823
Alabama | Muscle Shoals | 2788 | 1701 |  |  | Montgomery | 2183 | 2124 |  | Jonesboro | 4240 | 1934 |  | Alamosa | 8528 | 23
Alabama | Troy | 2196 | 2217 |  |  | Muscle Shoals | 2788 | 1701 |  | Little Rock | 3079 | 2076 |  | Aspen | 8294 | 68
Alabama | Tuscaloosa | 2656 | 2101 |  |  | Troy | 2196 | 2217 |  | Pine Bluff | 3384 | 2460 |  | Aurora CO | 6093 | 825
Aklaska | Adak | 9202 | 0 |  |  | Tuscaloosa | 2656 | 2101 |  | Rogers | 4327 | 1669 |  | Broomfield | 5836 | 637
Aklaska | Anchorage | 10158 | 0 |  | Aklaska | Adak | 9202 | 0 |  | Siloam Spring | 3868 | 1637 |  | Colorado Springs | 6115 | 481
Aklaska | Aniak | 11513 | 0 |  |  | Anchorage | 10158 | 0 |  | Springdale | 3963 | 1480 |  | Cortez | 5921 | 523
Aklaska | Annette Island | 6865 | 11 |  |  | Aniak | 11513 | 0 |  | Stuttgart | 2833 | 2120 |  | Craig | 8497 | 74
Aklaska | Anvik | 11628 | 27 |  |  | Annette Island | 6865 | 11 |  | Texarkana | 2471 | 2486 |  | Denver | 5655 | 923
Aklaska | Big River Lakes | 9868 | 1 |  |  | Anvik | 11628 | 27 |  | Walnut Ridge | 3733 | 1731 |  | Durango | 7114 | 312
Aklaska | Birchwood | 9521 | 1 |  |  | Big River Lakes | 9868 | 1 | California | Alturas | 6458 | 320 |  | Fort Collins | 7048 | 509
Aklaska | Chulitna | 10471 | 3 |  |  | Birchwood | 9521 | 1 |  | Bakersfield | 2013 | 2240 |  | Grand Junction | 5283 | 1230
Aklaska | Cold Bay | 9517 | 0 |  |  | Chulitna | 10471 | 3 |  | Bishop | 4053 | 1087 |  | Greeley | 6792 | 484
Aklaska | Cordova | 9376 | 0 |  |  | Cold Bay | 9517 | 0 |  | Blue Canyon | 5176 | 465 |  | Gunnison | 9306 | 13
Aklaska | Dillingham | 10504 | 1 |  |  | Cordova | 9376 | 0 |  | Blythe | 826 | 4527 |  | Gypsum | 7853 | 116
Aklaska | Dutch Harbor | 8963 | 0 |  |  | Dillingham | 10504 | 1 |  | Burbank | 1437 | 1449 |  | Hayden | 8169 | 211
Aklaska | Emmonak | 11775 | 0 |  |  | Dutch Harbor | 8963 | 0 |  | Camarillo | 1979 | 342 |  | La Junta | 5194 | 1318
Aklaska | Fairbanks | 13072 | 31 |  |  | Emmonak | 11775 | 0 |  | Camp Pendleton | 2499 | 731 |  | Lakewood | 6112 | 582
Aklaska | Gustavus | 9123 | 0 |  |  | Fairbanks | 13072 | 31 |  | Carlsbad CA | 1798 | 272 |  | Lamar | 5635 | 1305
Aklaska | Healy | 10689 | 0 |  |  | Gustavus | 9123 | 0 |  | Chino | 1609 | 1330 |  | Leadville | 10266 | 0
Aklaska | Homer | 9696 | 0 |  |  | Healy | 10689 | 0 |  | Chula Vista | 1642 | 410 |  | Limon | 6576 | 373
Aklaska | Hoonah | 8858 | 0 |  |  | Homer | 9696 | 0 |  | Concord CA | 2484 | 785 |  | Montrose | 5984 | 746
Aklaska | Hooper Bay | 11970 | 0 |  |  | Hoonah | 8858 | 0 |  | Crescent City | 4884 | 0 |  | Pueblo | 5178 | 936
Aklaska | Huslia | 13574 | 0 | ??? |  | Hooper Bay | 11970 | 0 |  | Daggett | 1931 | 3036 |  | Rifle | 5943 | 631
Aklaska | Iliamna | 9855 | 8 |  |  | Huslia | 13574 | 0 |  | Fairfield CA | 2708 | 1313 |  | Trinidad | 5266 | 798
Aklaska | Juneau | 8471 | 1 |  |  | Iliamna | 9855 | 8 |  | Fresno | 2327 | 2101 | Connecticut | Danbury | 6218 | 503
Aklaska | Kake | 8385 | 0 |  |  | Juneau | 8471 | 1 |  | Fullerton | 1312 | 1187 |  | Groton | 5700 | 418
Aklaska | Kenai | 10071 | 5 |  |  | Kake | 8385 | 0 |  | Hawthorne | 1299 | 570 |  | Hartford Brainard | 5969 | 731
Aklaska | Ketchikan | 8033 | 22 |  |  | Kenai | 10071 | 5 |  | Hayward | 2327 | 131 |  | New Haven | 5524 | 625
Aklaska | King Salmon | 10754 | 2 |  |  | Ketchikan | 8033 | 22 |  | Imperial CA | 837 | 4228 |  | Oxford | 6425 | 551
Aklaska | Kodiak | 8551 | 5 |  |  | King Salmon | 10754 | 2 |  | Lancaster CA | 2871 | 1983 |  | Stratford | 5530 | 738
Aklaska | Mekoryuk | 11572 | 0 |  |  | Kodiak | 8551 | 5 |  | Lemoore | 1654 | 1754 | Delaware | Dover | 4987 | 1010
Aklaska | Middleton Island | 8285 | 0 |  |  | Mekoryuk | 11572 | 0 |  | Livermore | 2933 | 679 |  | Wilmington DE | 5087 | 1088
Aklaska | Palmer | 8599 | 4 |  |  | Middleton Island | 8285 | 0 |  | Lompoc | 3256 | 27 | Florida | Crestview | 1672 | 2354
Aklaska | Petersburg AK | 8490 | 6 |  |  | Palmer | 8599 | 4 |  | Long Beach | 1136 | 995 |  | Daytona | 789 | 2857
Aklaska | Port Heiden | 10084 | 0 |  |  | Petersburg AK | 8490 | 6 |  | Los Angeles | 1283 | 617 |  | Fort Lauderdale | 322 | 4114
Aklaska | Saint Mary's | 11770 | 0 |  |  | Port Heiden | 10084 | 0 |  | McKinleyville | 4964 | 4 |  | Fort Myers | 205 | 4113
Aklaska | Sand Point | 9143 | 0 |  |  | Saint Mary's | 11770 | 0 |  | Merced | 2268 | 1389 |  | Fort Pierce | 722 | 2959
Aklaska | Seward | 9112 | 0 |  |  | Sand Point | 9143 | 0 |  | Modesto | 2211 | 1445 |  | Gainesville | 1306 | 2659
Aklaska | Sitka Japonski | 8002 | 0 |  |  | Seward | 9112 | 0 |  | Montague | 5097 | 567 |  | Homestead | 318 | 4117
Aklaska | Skagway | 8379 | 9 |  |  | Sitka Japonski | 8002 | 0 |  | Monterey | 3218 | 64 |  | Jacksonville FL | 1281 | 2565
Aklaska | Soldotna | 10146 | 3 |  |  | Skagway | 8379 | 9 |  | Napa | 3186 | 191 |  | Key West | 67 | 4906
Aklaska | St. Paul | 10607 | 0 |  |  | Soldotna | 10146 | 3 |  | Needles | 944 | 4672 |  | Lakeland | 973 | 3374
Aklaska | Talkeetna | 10973 | 2 |  |  | St. Paul | 10607 | 0 |  | Oakland | 2816 | 128 |  | Marathon | 124 | 5280
Aklaska | Togiac | 10391 | 3 |  |  | Talkeetna | 10973 | 2 |  | Oxnard | 2010 | 186 |  | Mayport | 1037 | 2806
Aklaska | Utqiagvik | 9862 | 0 |  |  | Togiac | 10391 | 3 |  | Palm Springs | 668 | 4333 |  | Melbourne | 369 | 3269
Aklaska | Valdez | 9257 | 0 |  |  | Utqiagvik | 9862 | 0 |  | Palmdale | 2829 | 1947 |  | Miami | 150 | 4292
Aklaska | Whittier | 9362 | 1 |  |  | Valdez | 9257 | 0 |  | Paso Robles | 2558 | 852 |  | Milton | 1728 | 2305
Aklaska | Wrangell | 7985 | 5 |  |  | Whittier | 9362 | 1 |  | Porterville | 2465 | 1620 |  | Naples | 289 | 3443
Aklaska | Yakutat | 9117 | 0 |  |  | Wrangell | 7985 | 5 |  | Red Bluff | 2782 | 1868 |  | Ocala | 1144 | 2724
Arizona | Casa Granda | 1473 | 3715 |  |  | Yakutat | 9117 | 0 |  | Redding | 2694 | 1688 |  | Orlando | 526 | 3234
Arizona | Douglas | 2328 | 1832 |  | Arizona | Casa Granda | 1473 | 3715 |  | Ridgecrest | 2782 | 3004 |  | Panama City | 1269 | 2877
Arizona | Flagstaff | 7112 | 110 |  |  | Douglas | 2328 | 1832 |  | Riverside | 1609 | 1413 |  | Pensacola | 1174 | 2711
Arizona | Grand Canyon | 6605 | 93 |  |  | Flagstaff | 7112 | 110 |  | Sacremento | 2581 | 1281 |  | Sarasota | 604 | 3266
Arizona | Kingman | 3005 | 2444 |  |  | Grand Canyon | 6605 | 93 |  | Salinas | 2852 | 84 |  | St. Petersburg | 429 | 3824
Arizona | Luke | 1137 | 4152 |  |  | Kingman | 3005 | 2444 |  | San Diego | 1019 | 742 |  | Tallahasse | 1545 | 2370
Arizona | Page | 3658 | 1967 |  |  | Luke | 1137 | 4152 |  | San Francisco | 2737 | 97 |  | Tampa | 646 | 3442
Arizona | Phoenix | 997 | 4591 |  |  | Page | 3658 | 1967 |  | San Jose | 2301 | 395 |  | Valparaiso | 2072 | 2339
Arizona | Prescott | 4146 | 1037 |  |  | Phoenix | 997 | 4591 |  | San Luis Obispo | 2325 | 201 |  | Vero Beach | 299 | 3489
Arizona | Safford | 1891 | 2760 |  |  | Prescott | 4146 | 1037 |  | Sandberg | 3610 | 1089 |  | West Palm Beach | 316 | 3787
Arizona | Scottsdale | 1214 | 4065 |  |  | Safford | 1891 | 2760 |  | Santa Anna | 1106 | 657 | Georgia | Albany GA | 1739 | 2456
Arizona | Show Low | 4515 | 643 |  |  | Scottsdale | 1214 | 4065 |  | Santa Barbara | 2433 | 104 |  | Alma | 2097 | 2316
Arizona | Tucson | 1596 | 3020 |  |  | Show Low | 4515 | 643 |  | Santa Maria | 2795 | 32 |  | Athens | 2730 | 1702
Arizona | Winslow | 4435 | 1247 |  |  | Tucson | 1596 | 3020 |  | Santa Monica | 1388 | 467 |  | Atlanta | 2773 | 1809
Arizona | Yuma | 535 | 4532 |  |  | Winslow | 4435 | 1247 |  | Santa Rose | 2859 | 329 |  | Augusta GA | 2512 | 2023
Arkansas | Batesville | 3761 | 1687 |  |  | Yuma | 535 | 4532 |  | South Lake Tahoe | 7847 | 11 |  | Brunswick GA | 2102 | 2568
Arkansas | Bentonville | 4394 | 1514
Arkansas | El Dorado | 2672 | 2512 |  | State | City | HDD | CDD | State | City | HDD | CDD | State | City | HDD | CDD
Arkansas | Fayetteville AR | 3726 | 1753 |  |  | Columbus GA | 2063 | 2407 |  | Fairfield IA | 6031 | 1093 |  | Millinocket | 7921 | 323
Arkansas | Flippin | 3724 | 1604 |  |  | Macon | 2400 | 2182 |  | Fort Dodge | 7177 | 825 |  | Portland ME | 7679 | 335
Arkansas | Fort Smith | 3596 | 2020 |  |  | Marietta | 3734 | 1401 |  | Fort Madison | 5277 | 1148 |  | Presque Isle | 9295 | 168
Arkansas | Harrison | 3822 | 1590 |  |  | Rome | 3331 | 1895 |  | Keokuk | 5496 | 1208 |  | Rockland | 7451 | 194
Arkansas | Hot Springs AR | 3256 | 2111 |  |  | Savannah | 1759 | 2474 |  | Knoxville IA | 5891 | 1265 |  | Sanford | 7774 | 259
Arkansas | Jonesboro | 4240 | 1934 |  |  | Valdosta | 1525 | 2860 |  | Le Mars | 6122 | 871 |  | Waterville | 7926 | 367
Arkansas | Little Rock | 3079 | 2076 |  |  | Warner Robins | 2983 | 2069 |  | Mason City | 7927 | 639 |  | Wiscasset | 6877 | 350
Arkansas | Pine Bluff | 3384 | 2460 |  | Hawaii | Hilo | 0 | 3279 |  | Monticello IA | 6857 | 744 | Maryland | Baltimore | 4631 | 1237
Arkansas | Rogers | 4327 | 1669 |  |  | Honolulu | 0 | 4561 |  | Muscatine | 6206 | 1026 |  | Camp Springs | 4652 | 1178
Arkansas | Siloam Spring | 3868 | 1637 |  |  | Kahului | 0 | 3999 |  | Newton IA | 6207 | 816 |  | Hagerstown | 4867 | 1079
Arkansas | Springdale | 3963 | 1480 |  |  | Kalaoa | 0 | 4325 |  | Oelwen | 6483 | 644 |  | Lexington Park | 3556 | 1404
Arkansas | Stuttgart | 2833 | 2120 |  |  | Kaneohe | 0 | 4485 |  | Orange City | 6867 | 865 |  | Salisbury | 3910 | 1229
Arkansas | Texarkana | 2471 | 2486 |  |  | Kapalua | 0 | 3908 |  | Ottumwa | 6647 | 875 | Massachusetts | Beverly | 6669 | 492
Arkansas | Walnut Ridge | 3733 | 1731 |  |  | Kapolei | 12 | 4410 |  | Red Oak | 5959 | 1203 |  | Boston | 5793 | 734
California | Alturas | 6458 | 320 |  |  | Lanai | 22 | 2590 |  | Sheldon | 6939 | 723 |  | Chicopee Falls | 6354 | 507
California | Bakersfield | 2013 | 2240 |  |  | Lihue | 0 | 3919 |  | Shenandoah | 6233 | 1258 |  | Hyannis | 5749 | 436
California | Bishop | 4053 | 1087 |  |  | Molokai | 97 | 3734 |  | Sioux City | 6796 | 936 |  | Lawrence | 5940 | 559
California | Blue Canyon | 5176 | 465 |  | Idaho | Boise | 5395 | 756 |  | Spencer | 8206 | 592 |  | Marthas Vineyard | 5622 | 361
California | Blythe | 826 | 4527 |  |  | Burley | 6225 | 927 |  | Storm Lake | 6982 | 821 |  | Mashpee | 6062 | 565
California | Burbank | 1437 | 1449 |  |  | Caldwell | 5803 | 636 |  | Washington IA | 6249 | 991 |  | Nantucket | 5350 | 298
California | Camarillo | 1979 | 342 |  |  | Coeur d'Alene | 6897 | 344 |  | Waterloo | 7257 | 827 |  | New Bedford | 5724 | 577
California | Camp Pendleton | 2499 | 731 |  |  | Grand View | 6105 | 834 |  | Webster City | 6376 | 1099 |  | North Adams | 6626 | 319
California | Carlsbad CA | 1798 | 272 |  |  | Hailey | 7160 | 679 | Kansas | Chanute | 4458 | 1804 |  | Norwood | 6177 | 637
California | Chino | 1609 | 1330 |  |  | Idaho Falls | 7769 | 246 |  | Concordia | 4890 | 1632 |  | Plymouth | 5889 | 374
California | Chula Vista | 1642 | 410 |  |  | Lewiston | 5457 | 885 |  | Dodge City | 4969 | 1457 |  | Provincetown | 5705 | 595
California | Concord CA | 2484 | 785 |  |  | Malad City | 6681 | 546 |  | Emporia | 5717 | 1458 |  | Westfield | 6623 | 494
California | Crescent City | 4884 | 0 |  |  | Pocatello | 7100 | 393 |  | Garden City | 5180 | 1240 |  | Worchester | 7164 | 346
California | Daggett | 1931 | 3036 |  |  | Salmon | 7482 | 309 |  | Goodland | 5915 | 915 | Michigan | Alpena | 8250 | 290
California | Fairfield CA | 2708 | 1313 |  |  | Soda Springs | 8439 | 198 |  | Great Bend | 4891.5 | 1417 |  | Ann Arbor | 6487 | 492
California | Fresno | 2327 | 2101 |  |  | Twin Falls | 6148 | 733 |  | Hays | 5021 | 1558 |  | Battle Creek | 6210 | 639
California | Fullerton | 1312 | 1187 |  | Illinois | Aurora IL | 6790 | 683 |  | Hill City | 5597 | 1192 |  | Benton Harbor | 6588 | 810
California | Hawthorne | 1299 | 570 |  |  | Belleville | 5320 | 1245 |  | Hutchinson KS | 4591 | 1552 |  | Cadillac | 7905 | 373
California | Hayward | 2327 | 131 |  |  | Bloomington IL | 6112 | 847 |  | Junction City | 4528 | 1600 |  | Calumet | 8988 | 239
California | Imperial CA | 837 | 4228 |  |  | Bondville | 5747 | 1021 |  | Liberal | 4810 | 1410 |  | Detroit | 6621 | 679
California | Lancaster CA | 2871 | 1983 |  |  | Chicago | 6399 | 830 |  | Manhattan | 5013 | 1652 |  | Escanaba | 8796 | 131
California | Lemoore | 1654 | 1754 |  |  | Decatur | 5546 | 1166 |  | Newton KS | 5023 | 1400 |  | Flint | 6977 | 515
California | Livermore | 2933 | 679 |  |  | Marion IL | 4674 | 1330 |  | Olathe | 4598 | 1437 |  | Freeland | 7059 | 524
California | Lompoc | 3256 | 27 |  |  | Moline | 6459 | 980 |  | Russell | 5005 | 1436 |  | Grand Rapids MI | 6908 | 579
California | Long Beach | 1136 | 995 |  |  | Mount Vernon | 4817 | 1412 |  | Salina | 4660 | 1787 |  | Houghton Lake | 8067 | 316
California | Los Angeles | 1283 | 617 |  |  | Murphysboro | 4380 | 1633 |  | Topeka | 4953 | 1315 |  | Howell | 6295 | 899
California | McKinleyville | 4964 | 4 |  |  | Peoria | 6229 | 888 |  | Wichita | 4324 | 1554 |  | Ironwood | 9090 | 348
California | Merced | 2268 | 1389 |  |  | Quincy | 5233 | 1067 | Kentucky | Bowling Green | 4380 | 1410 |  | Jackson MI | 6385 | 715
California | Modesto | 2211 | 1445 |  |  | Rock Falls | 6269 | 785 |  | Fort Knox | 4918 | 1283 |  | Kalamazoo | 6196 | 599
California | Montague | 5097 | 567 |  |  | Rockford | 7237 | 778 |  | Hebron | 5288 | 962 |  | Kincheloe | 9193 | 115
California | Monterey | 3218 | 64 |  |  | Springfield IL | 5527 | 1166 |  | Henderson City | 5049 | 995 |  | Kingsford | 8327 | 432
California | Napa | 3186 | 191 |  |  | West Chicago | 6194 | 830 |  | Hopkinsville | 4484 | 1620 |  | Lansing | 7045 | 597
California | Needles | 944 | 4672 |  | Indiana | Bloomington IN | 5385 | 1025 |  | Jackson KY | 3869 | 1098 |  | Manistee | 7343 | 582
California | Oakland | 2816 | 128 |  |  | Evansville | 4474 | 1376 |  | Lexington | 4856 | 1104 |  | Marie | 9162 | 113
California | Oxnard | 2010 | 186 |  |  | Fort Wayne | 6471 | 764 |  | London | 4529 | 988 |  | Menominee | 7783 | 452
California | Palm Springs | 668 | 4333 |  |  | Huntingburg | 4223 | 1448 |  | Louisville | 4521 | 1449 |  | Mount Clemens | 6040 | 597
California | Palmdale | 2829 | 1947 |  |  | Indianapolis | 5845 | 1044 |  | Somerset | 3916 | 1550 |  | Muskegon | 7018 | 502
California | Paso Robles | 2558 | 852 |  |  | Kokomo | 5957 | 822 |  | West Paducah | 3811 | 1439 |  | Oscoda | 7315 | 455
California | Porterville | 2465 | 1620 |  |  | Lafayette IN | 5967 | 971 | Louisiana | Alexandria LA | 1136 | 2477 |  | Pellston | 7426 | 360
California | Red Bluff | 2782 | 1868 |  |  | Muncie | 5626 | 1004 |  | Baton Rouge | 1762 | 2622 |  | Port Huron | 6522 | 705
California | Redding | 2694 | 1688 |  |  | South Bend | 5956 | 860 |  | Bossier City | 2562 | 2270 |  | Traverse City | 7754 | 370
California | Ridgecrest | 2782 | 3004 |  |  | Terre Haute | 5135 | 1290 |  | Houma | 1677 | 2848 |  | Waterford Township | 6152 | 772
California | Riverside | 1609 | 1413 |  | Iowa | Algona | 6847 | 707 |  | Lafayette LA | 1590 | 2699 | Minnesota | Aitkin | 9304 | 194
California | Sacremento | 2581 | 1281 |  |  | Atlantic | 6656 | 865 |  | Lake Charles | 1635 | 2596 |  | Albert Lea | 7196 | 920
California | Salinas | 2852 | 84 |  |  | Boone | 6699 | 897 |  | Leesville | 2197 | 2514 |  | Alexandria MN | 8895 | 535
California | San Diego | 1019 | 742 |  |  | Burlington IA | 5680 | 1465 |  | Monroe | 2229 | 2270 |  | Austin MN | 7892 | 529
California | San Francisco | 2737 | 97 |  |  | Carroll | 6880 | 899 |  | New Iberia | 1717 | 2559 |  | Baudette | 8804 | 112
California | San Jose | 2301 | 395 |  |  | Cedar Rapids | 6900 | 714 |  | New Orleans | 1358 | 2784 |  | Bemidji | 9161 | 333
California | San Luis Obispo | 2325 | 201 |  |  | Chariton | 6028 | 1252 |  | Patterson | 1452 | 2571 |  | Benson | 8676 | 659
California | Sandberg | 3610 | 1089 |  |  | Charles City | 6765 | 733 |  | Pineville | 2109 | 2421 |  | Brainerd | 8713 | 322
California | Santa Anna | 1106 | 657 |  |  | Clarinda | 6072 | 1319 |  | Shreveport | 2351 | 2384 |  | Cambridge | 8823 | 405
California | Santa Barbara | 2433 | 104 |  |  | Clinton IA | 6895 | 1019 | Maine | Auburn ME | 7691 | 303 |  | Cloquet | 9368 | 258
California | Santa Maria | 2795 | 32 |  |  | Council Bluffs | 5864 | 969 |  | Augusta ME | 7495 | 396 |  | Crane Lake | 10240 | 164
California | Santa Monica | 1388 | 467 |  |  | Creston | 6150 | 983 |  | Bangor | 7671 | 450 |  | Crookston | 9095 | 348
California | Santa Rose | 2859 | 329 |  |  | Decorah | 6125 | 978 |  | Bar Harbor | 8037 | 71 |  | Detroit Lakes | 8704 | 460
California | South Lake Tahoe | 7847 | 11 |  |  | Denison | 6571 | 1057 |  | Brunswick ME | 7456 | 373 |  | Duluth | 9620 | 159
California | Stockton | 2494 | 1296 |  |  | Des Moines | 6493 | 1121 |  | Caribou | 9841 | 171 |  | Ely | 9501 | 186
California | Truckee | 7884 | 87 |  |  | Dubuque | 7516 | 525 |  | Frenchville | 9765 | 164 |  | Eveleth | 9987 | 255
California | Twentynine Palms | 1788 | 3297 |  |  | Estherville | 8458 | 551 |  | Houlton | 9255 | 206 |  | Fairmont | 7586 | 652
California | Ukiah | 2981 | 874
California | Van Nuys | 1214 | 1507 |  | State | City | HDD | CDD | State | City | HDD | CDD | State | City | HDD | CDD
California | Visalia | 3032 | 1602 |  |  | Faribault | 7497 | 504 |  | Livingston | 7111 | 370 |  | Buffalo | 6612 | 468
California | Yuba City | 2533 | 1476 |  |  | Fergus Falls | 7838 | 841 |  | Miles City | 7617 | 648 |  | Elmira | 6449 | 297
Colorado | Akron CO | 6087 | 823 |  |  | Flying Cloud | 7921 | 958 |  | Missoula | 7323 | 269 |  | Glen Falls | 7158 | 481
Colorado | Alamosa | 8528 | 23 |  |  | Fosston | 9746 | 252 |  | Sidney MT | 9396 | 411 |  | Jamestown NY | 7188 | 278
Colorado | Aspen | 8294 | 68 |  |  | Glenwood | 8440 | 528 |  | Wolf Point | 8983 | 249 |  | Massena | 8046 | 376
Colorado | Aurora CO | 6093 | 825 |  |  | Grand Rapids MN | 9137 | 306 | Nebraska | Ainsworth | 6118 | 789 |  | Monticello NY | 7059 | 428
Colorado | Broomfield | 5836 | 637 |  |  | Hallock | 9445 | 460 |  | Alliance | 7026 | 736 |  | New Windsor | 6159 | 756
Colorado | Colorado Springs | 6115 | 481 |  |  | Hibbing | 9987 | 219 |  | Beatrice | 5646 | 1135 |  | New York | 4885 | 1133
Colorado | Cortez | 5921 | 523 |  |  | Hutchinson MN | 8330 | 620 |  | Bellevue | 6309 | 1139 |  | Nigara Falls | 6484 | 602
Colorado | Craig | 8497 | 74 |  |  | International Falls | 10382 | 259 |  | Broken Bow | 6772 | 790 |  | Republic | 4893 | 983
Colorado | Denver | 5655 | 923 |  |  | Litchfield | 7734 | 543 |  | Chadron | 6543 | 812 |  | Rockester | 6518 | 627
Colorado | Durango | 7114 | 312 |  |  | Little Falls | 9240 | 385 |  | Columbus NC | 6670 | 937 |  | Ronkonkoma | 5005 | 983
Colorado | Fort Collins | 7048 | 509 |  |  | Mankato | 7716 | 645 |  | Falls City | 5775 | 1039 |  | Saranac Lake | 9158 | 149
Colorado | Grand Junction | 5283 | 1230 |  |  | Marshall | 7740 | 688 |  | Fremont | 6953 | 935 |  | Syracuse | 6609 | 535
Colorado | Greeley | 6792 | 484 |  |  | Minneapolis | 7783 | 731 |  | Grand Island | 6654 | 1041 |  | Utica | 6974 | 414
Colorado | Gunnison | 9306 | 13 |  |  | Mora | 8665 | 364 |  | Hastings | 6075 | 1108 |  | Wappingers Falls | 6030 | 607
Colorado | Gypsum | 7853 | 116 |  |  | Morris | 8849 | 375 |  | Holdrege | 6510 | 852 |  | Watertown NY | 7496 | 330
Colorado | Hayden | 8169 | 211 |  |  | New Ulm | 7646 | 641 |  | Imperial NE | 5834 | 1024 |  | Westhampton Beach | 5741 | 455
Colorado | La Junta | 5194 | 1318 |  |  | Orr | 10534 | 152 |  | Kearney | 6348 | 843 |  | White Plains | 5783 | 595
Colorado | Lakewood | 6112 | 582 |  |  | Owatonna | 7788 | 641 |  | Lincoln | 5892 | 1220 | North Carolina | Asheville | 4273 | 817
Colorado | Lamar | 5635 | 1305 |  |  | Park Rapids | 9215 | 236 |  | McCook | 5616 | 1256 |  | Cape Hatteras | 2563 | 1729
Colorado | Leadville | 10266 | 0 |  |  | Pipestone | 8624 | 649 |  | Norfolk NE | 6943 | 986 |  | Charlotte | 3153 | 1675
Colorado | Limon | 6576 | 373 |  |  | Red Wing | 7935 | 761 |  | North Platte | 6556 | 802 |  | Elizabeth City | 2744 | 1760
Colorado | Montrose | 5984 | 746 |  |  | Redwood Falls | 7938 | 609 |  | Omaha | 5954 | 1275 |  | Fayetteville NC | 3489 | 1576
Colorado | Pueblo | 5178 | 936 |  |  | Rochester | 8386 | 488 |  | O'Neill | 7733 | 847 |  | Goldsboro | 3589 | 1743
Colorado | Rifle | 5943 | 631 |  |  | Roseau | 9817 | 162 |  | Ord | 6279 | 872 |  | Greensboro | 3868 | 1371
Colorado | Trinidad | 5266 | 798 |  |  | Silver Bay | 10453 | 59 |  | Scottsbluff | 6560 | 760 |  | Greenville NC | 3040 | 1603
Connecticut | Danbury | 6218 | 503 |  |  | St Cloud | 9020 | 444 |  | Sidney NE | 6864 | 494 |  | Havelock | 3345 | 1701
Connecticut | Groton | 5700 | 418 |  |  | St Paul | 8019 | 587 |  | Tekamah | 6650 | 1005 |  | Hickory | 3457 | 1416
Connecticut | Hartford Brainard | 5969 | 731 |  |  | Thief River Falls | 9328 | 341 |  | Valentine | 6453 | 811 |  | Jacksonville NC | 3814 | 1370
Connecticut | New Haven | 5524 | 625 |  |  | Two Harbors | 9412 | 190 | Nevada | Elko | 7070 | 407 |  | Kinston | 3397 | 1818
Connecticut | Oxford | 6425 | 551 |  |  | Wheaton | 8713 | 496 |  | Ely | 7267 | 154 |  | Manteo | 3053 | 1617
Connecticut | Stratford | 5530 | 738 |  |  | Willmar | 7649 | 581 |  | Fallon | 5163 | 1010 |  | New Bern | 2276 | 1874
Delaware | Dover | 4987 | 1010 |  |  | Winona | 7711 | 633 |  | Las Vegas NV | 2301 | 3187 |  | Raleigh | 3465 | 1566
Delaware | Wilmington DE | 5087 | 1088 |  |  | Worthington | 7750 | 644 |  | Lovelock | 5351 | 836 |  | Rocky Mount | 2878 | 1435
Florida | Crestview | 1672 | 2354 |  | Mississippi | Biloxi | 1928 | 2606 |  | Mercury | 3001 | 2396 |  | Southern Pines | 3570 | 1496
Florida | Daytona | 789 | 2857 |  |  | Columbus MS | 3394 | 2077 |  | Reno | 5488 | 620 |  | Wilmington NC | 2401 | 1928
Florida | Fort Lauderdale | 322 | 4114 |  |  | Greenville MS | 2432 | 2468 |  | Tonopah | 5431 | 747 |  | Winston-Salem | 3214 | 1244
Florida | Fort Myers | 205 | 4113 |  |  | Greenwood | 2552 | 2164 |  | Winnemucca | 6158 | 567 | North Dakota | Bismarck | 8452 | 453
Florida | Fort Pierce | 722 | 2959 |  |  | Gulfport | 1619 | 2565 | New Hampshire | Berlin | 8891 | 145 |  | Devils Lake | 9251 | 288
Florida | Gainesville | 1306 | 2659 |  |  | Hattiesburg | 2274 | 2071 |  | Concord NH | 7479 | 397 |  | Dickinson | 9028 | 417
Florida | Homestead | 318 | 4117 |  |  | Jackson MS | 2428 | 2237 |  | Keene | 7169 | 470 |  | Fargo | 9211 | 491
Florida | Jacksonville FL | 1281 | 2565 |  |  | McComb | 2086 | 2315 |  | Laconia | 7198 | 396 |  | Grand Forks | 9534 | 486
Florida | Key West | 67 | 4906 |  |  | Meridian | 2417 | 2038 |  | Lebanon | 7349 | 389 |  | Jamestown ND | 9505 | 519
Florida | Lakeland | 973 | 3374 |  |  | Natchez | 1915 | 2060 |  | Manchester | 6322 | 664 |  | Minot | 8972 | 432
Florida | Marathon | 124 | 5280 |  |  | Starkville | 3378 | 1962 |  | Mount Washington | 13275 | 0 |  | Williston | 8467 | 404
Florida | Mayport | 1037 | 2806 |  |  | Tupelo | 3039 | 1905 |  | Portsmouth | 6753 | 527 | Ohio | Akron OH | 259 | 654
Florida | Melbourne | 369 | 3269 |  | Missouri | Cape Girardeau | 4506 | 1289 | New Jersey | Atlantic City | 5073 | 886 |  | Cincinnati | 4911 | 1039
Florida | Miami | 150 | 4292 |  |  | Columbia MO | 5307 | 1190 |  | Belmar | 5280 | 890 |  | Cleveland | 6160 | 760
Florida | Milton | 1728 | 2305 |  |  | Farmington MO | 4527 | 1190 |  | Fairfield NJ | 5060 | 654 |  | Columbus OH | 5599 | 747
Florida | Naples | 289 | 3443 |  |  | Ft. Leonard Wood | 4675 | 1496 |  | Millville | 4680 | 1011 |  | Dayton | 5945 | 905
Florida | Ocala | 1144 | 2724 |  |  | Jefferson City | 4504 | 1469 |  | Newark | 5057 | 1237 |  | Findlay | 5590 | 541
Florida | Orlando | 526 | 3234 |  |  | Joplin | 3663 | 1949 |  | Rio Grande | 4286 | 1028 |  | Mansfield | 6615 | 620
Florida | Panama City | 1269 | 2877 |  |  | Kaiser | 4634 | 1528 |  | Teterboro | 4868 | 695 |  | Toledo OH | 6515 | 610
Florida | Pensacola | 1174 | 2711 |  |  | Kansas City | 5434 | 1316 |  | Trenton | 5040 | 1177 |  | Youngstown | 6628 | 531
Florida | Sarasota | 604 | 3266 |  |  | Kirksville | 6397 | 1047 | New Mexico | Alamogordo | 3327 | 1793 |  | Zanesville | 4941 | 702
Florida | St. Petersburg | 429 | 3824 |  |  | Poplar Bluff | 4108 | 1592 |  | Albuquerque | 4157 | 1269 | Oklahoma | Altus | 3164 | 2563
Florida | Tallahasse | 1545 | 2370 |  |  | Springfield MO | 4629 | 1307 |  | Carlsbad NM | 2764 | 2298 |  | Bartlesville | 4266 | 1654
Florida | Tampa | 646 | 3442 |  |  | St. Joseph | 5495 | 1379 |  | Clayton | 4765 | 1156 |  | Clinton OK | 4175 | 2023
Florida | Valparaiso | 2072 | 2339 |  |  | St. Louis | 4846 | 1555 |  | Clovis | 4467 | 1396 |  | Enid | 4466 | 2034
Florida | Vero Beach | 299 | 3489 |  |  | Vichy | 4729 | 924 |  | Deming | 2878 | 1891 |  | Fort Sill | 3421 | 2392
Florida | West Palm Beach | 316 | 3787 |  |  | Warrensburg | 4803 | 1344 |  | Farmington NM | 5199 | 1022 |  | Gage | 4103 | 2013
Georgia | Albany GA | 1739 | 2456 |  | Montana | Billings | 6731 | 548 |  | Gallup | 6002 | 388 |  | Hobart | 3600 | 2377
Georgia | Alma | 2097 | 2316 |  |  | Bozeman | 8354 | 282 |  | Las Cruces | 2876 | 2146 |  | Lawton | 3055 | 1979
Georgia | Athens | 2730 | 1702 |  |  | Butte | 9089 | 101 |  | Las Vegas NM | 5180 | 307 |  | McAlester | 3081 | 2086
Georgia | Atlanta | 2773 | 1809 |  |  | Cut Bank | 8186 | 86 |  | Roswell | 2735 | 1932 |  | Oklahoma City | 3556 | 2038
Georgia | Augusta GA | 2512 | 2023 |  |  | Glasgow | 8163 | 504 |  | Ruidoso | 4095 | 604 |  | Ponca City | 3887 | 2437
Georgia | Brunswick GA | 2102 | 2568 |  |  | Glendive | 8667 | 555 |  | Santa Fe | 5449 | 589 |  | Stillwater | 3799 | 2185
Georgia | Columbus GA | 2063 | 2407 |  |  | Great Falls | 7854 | 344 |  | Taos | 6904 | 198 |  | Tulsa | 3844 | 2066
Georgia | Macon | 2400 | 2182 |  |  | Havre | 8213 | 432 |  | Truth or Consequences | 3102 | 1742 | Oregon | Astoria | 4933 | 48
Georgia | Marietta | 3734 | 1401 |  |  | Helena | 7587 | 320 |  | Tucumcari | 4109 | 1423 |  | Aurora OR | 4277 | 327
Georgia | Rome | 3331 | 1895 |  |  | Kalispell | 7928 | 126 | New York | Albany NY | 6773 | 489 |  | Baker City | 7142 | 231
Georgia | Savannah | 1759 | 2474 |  |  | Lewistown | 8014 | 107 |  | Binghamton | 7015 | 404 |  | Burns | 7201 | 230
Georgia | Valdosta | 1525 | 2860
Georgia | Warner Robins | 2983 | 2069 |  | State | City | HDD | CDD | State | City | HDD | CDD | State | City | HDD | CDD
Hawaii | Hilo | 0 | 3279 |  |  | Corvallus | 4257 | 405 |  | Del Rio | 1340 | 3187 |  | Weyers Cave | 4878 | 1102
Hawaii | Honolulu | 0 | 4561 |  |  | Eugene | 4803 | 295 |  | El Paso | 2499 | 2171 |  | Winchester | 5193 | 1196
Hawaii | Kahului | 0 | 3999 |  |  | Klamath Falls | 6765 | 185 |  | Galveston | 1096 | 3116 |  | Wise | 4910 | 747
Hawaii | Kalaoa | 0 | 4325 |  |  | La Grande | 6152 | 329 |  | Georgetown | 2070 | 2683 | Washington | Aberdeen WA
Hawaii | Kaneohe | 0 | 4485 |  |  | Lakeview | 7091 | 199 |  | Greenville TX | 2717 | 2445 |  | Bellingham | 5768 | 24
Hawaii | Kapalua | 0 | 3908 |  |  | Medford | 4530 | 602 |  | Harlingen | 518 | 3816 |  | Bremerton | 5533 | 112
Hawaii | Kapolei | 12 | 4410 |  |  | North Bend | 4525 | 0 |  | Hondo | 1694 | 2825 |  | Ephrata | 5578 | 882
Hawaii | Lanai | 22 | 2590 |  |  | Pendleton | 5204 | 585 |  | Houston | 1439 | 2974 |  | Everett | 5097 | 69
Hawaii | Lihue | 0 | 3919 |  |  | Portland OR | 4187 | 367 |  | Killeen | 2087 | 2721 |  | Forks | 5682 | 19
Hawaii | Molokai | 97 | 3734 |  |  | Redmond | 6583 | 204 |  | Kingsville | 895 | 3419 |  | Hanford | 5669 | 1007
Idaho | Boise | 5395 | 756 |  |  | Roseburg | 3798 | 405 |  | Laredo | 1164 | 4080 |  | Hoquiam | 5240 | 21
Idaho | Burley | 6225 | 927 |  |  | Salem | 4583 | 275 |  | Longview | 2131 | 2437 |  | Kelso | 4682 | 115
Idaho | Caldwell | 5803 | 636 |  |  | Sexton Summit | 5657 | 362 |  | Lubbock | 3436 | 1699 |  | Moses Lake | 5431 | 641
Idaho | Coeur d'Alene | 6897 | 344 |  | Pennsylvania | Allentown | 5651 | 773 |  | Lufkin | 1823 | 2479 |  | Olympia | 5331 | 118
Idaho | Grand View | 6105 | 834 |  |  | Altoona | 5917 | 595 |  | Marfa | 3117 | 1044 |  | Pasco | 4921 | 711
Idaho | Hailey | 7160 | 679 |  |  | Bradford | 8204 | 204 |  | McAllen | 729 | 3903 |  | Port Angeles | 5945 | 13
Idaho | Idaho Falls | 7769 | 246 |  |  | Butler | 6575 | 481 |  | McGregor | 2334 | 2614 |  | Pullman | 6483 | 234
Idaho | Lewiston | 5457 | 885 |  |  | DuBois | 6942 | 386 |  | Midland | 2482 | 2057 |  | Renton | 4378 | 216
Idaho | Malad City | 6681 | 546 |  |  | Erie | 6460 | 579 |  | Mineral wells | 2363 | 2495 |  | Seattle | 4372 | 169
Idaho | Pocatello | 7100 | 393 |  |  | Franklin PA | 6830 | 327 |  | Nacogdockes | 2305 | 2313 |  | Spokane | 6716 | 341
Idaho | Salmon | 7482 | 309 |  |  | Harrisburg | 5409 | 927 |  | Palacios | 1346 | 3024 |  | Stampede Pass | 8898 | 81
Idaho | Soda Springs | 8439 | 198 |  |  | Johnstown | 6516 | 482 |  | Paris | 3100 | 2057 |  | Tacoma | 5664 | 142
Idaho | Twin Falls | 6148 | 733 |  |  | Lancaster PA | 4955 | 877 |  | Port Arthur | 1422 | 2904 |  | The Dalles | 4501 | 879
Illinois | Aurora IL | 6790 | 683 |  |  | Middletown | 6105 | 1123 |  | Rockport | 691 | 3576 |  | Toledo WA | 5853 | 82
Illinois | Belleville | 5320 | 1245 |  |  | Philadelphia | 4824 | 1184 |  | San Angelo | 2485 | 2259 |  | Walla Walla | 4836 | 839
Illinois | Bloomington IL | 6112 | 847 |  |  | Pittsburgh | 5925 | 726 |  | San Antonio | 1548 | 2992 |  | Wenatchee | 5748 | 867
Illinois | Bondville | 5747 | 1021 |  |  | Reading | 5067 | 900 |  | Temple | 2260 | 2717 |  | Whidbey Island | 5510 | 0
Illinois | Chicago | 6399 | 830 |  |  | Scranton | 5216 | 608 |  | Tyler | 2339 | 2363 |  | Yakima | 6041 | 430
Illinois | Decatur | 5546 | 1166 |  |  | University Park | 6188 | 585 |  | Victoria | 1309 | 3042 | West Virginia | Beckley | 5361 | 631
Illinois | Marion IL | 4674 | 1330 |  |  | Washington PA | 5727 | 528 |  | Waco | 2251 | 2699 |  | Bluefield | 4451 | 597
Illinois | Moline | 6459 | 980 |  |  | Williamsport | 5761 | 759 |  | Wichita Falls | 2838 | 2350 |  | Bridgeport | 5137 | 855
Illinois | Mount Vernon | 4817 | 1412 |  | Rhode Island | New Shoreham | 5221 | 435 |  | Wink | 2423 | 2932 |  | Charleston WV | 4708 | 1015
Illinois | Murphysboro | 4380 | 1633 |  |  | Pawtucket | 6466 | 504 | Utah | Blanding | 5535 | 1171 |  | Elkins | 6050 | 368
Illinois | Peoria | 6229 | 888 |  |  | Providence | 5870 | 735 |  | Bryce Canyon City | 8955 | 33 |  | Huntington | 4642 | 1077
Illinois | Quincy | 5233 | 1067 |  | South Carolina | Anderson | 3436 | 1037 |  | Cedar City | 5776 | 747 |  | Lewisburg | 6270 | 432
Illinois | Rock Falls | 6269 | 785 |  |  | Beaufort | 2096 | 2158 |  | Delta | 6021 | 799 |  | Martinsburg | 4345 | 761
Illinois | Rockford | 7237 | 778 |  |  | Charleston SC | 2051 | 2302 |  | Hanksville | 5354 | 1445 |  | Morgantown | 5020 | 669
Illinois | Springfield IL | 5527 | 1166 |  |  | Columbia SC | 2593 | 2020 |  | Moab | 5106 | 1301 |  | Parkersburg | 4979 | 1101
Illinois | West Chicago | 6194 | 830 |  |  | Florence | 2316 | 2202 |  | Ogden | 5831 | 1092 |  | Wheeling | 5793 | 639
Indiana | Bloomington IN | 5385 | 1025 |  |  | Greenville SC | 3652 | 1409 |  | Provo | 5836 | 858 | Wisconsin | Antigo | 8664 | 440
Indiana | Evansville | 4474 | 1376 |  |  | Greer | 3244 | 1553 |  | Saint George | 2729 | 2936 |  | Appleton | 7022 | 517
Indiana | Fort Wayne | 6471 | 764 |  |  | Myrtle Beach | 2379 | 1870 |  | Salt Lake City | 5350 | 1118 |  | Eau Claire | 8475 | 600
Indiana | Huntingburg | 4223 | 1448 |  |  | North Myrtle Beach | 2470 | 1727 |  | Vernal | 6661 | 525 |  | Green Bay | 7853 | 496
Indiana | Indianapolis | 5845 | 1044 |  |  | Sumter | 3072 | 1706 |  | Wendover | 5970 | 1221 |  | Janesville | 6713 | 295
Indiana | Kokomo | 5957 | 822 |  | South Dakota | Aberdeen SD | 7968 | 657 | Vermont | Burlington VT | 7491 | 420 |  | La Crosse | 7445 | 748
Indiana | Lafayette IN | 5967 | 971 |  |  | Brookings | 7926 | 449 |  | Montpelier | 7662 | 249 |  | Lone Rock | 6651 | 543
Indiana | Muncie | 5626 | 1004 |  |  | Huron | 8196 | 638 |  | Rutland | 7563 | 485 |  | Madison | 7724 | 604
Indiana | South Bend | 5956 | 860 |  |  | Mitchell | 7879 | 909 |  | Springfield VT | 7264 | 281 |  | Manitowac | 7231 | 322
Indiana | Terre Haute | 5135 | 1290 |  |  | Mobridge | 8474 | 735 | Virginia | Abingdon | 4953 | 1011 |  | Marshfield | 7449 | 432
Iowa | Algona | 6847 | 707 |  |  | Pierre | 7079 | 818 |  | Blacksburg | 5081 | 754 |  | Milwaukee | 7348 | 545
Iowa | Atlantic | 6656 | 865 |  |  | Rapid City | 7203 | 675 |  | Charlottesville | 3697 | 1122 |  | Minocqua | 8772 | 410
Iowa | Boone | 6699 | 897 |  |  | Sioux Falls | 7680 | 680 |  | Danville | 3707 | 1678 |  | Mosinee | 8719 | 401
Iowa | Burlington IA | 5680 | 1465 |  |  | Watertown SD | 8803 | 422 |  | Farmville | 4084 | 1323 |  | Oshkosh | 8013 | 380
Iowa | Carroll | 6880 | 899 |  |  | Yankton | 7058 | 996 |  | Franklin VA | 3096 | 1557 |  | Phillips | 8638 | 337
Iowa | Cedar Rapids | 6900 | 714 |  | Tennessee | Blountville | 4439 | 971 |  | Fredericksburg | 4531 | 1420 |  | Rhinelander | 8823 | 437
Iowa | Chariton | 6028 | 1252 |  |  | Chattanooga | 3224 | 1657 |  | Hampton | 4195 | 1437 |  | Rice Lake | 8706 | 420
Iowa | Charles City | 6765 | 733 |  |  | Crossville | 3976 | 933 |  | Hillsville | 5459 | 604 |  | Sturgeon Bay | 7301 | 424
Iowa | Clarinda | 6072 | 1319 |  |  | Dyersburg | 3723 | 1896 |  | Hot Springs VA | 6585 | 254 |  | Watertown WI | 6864 | 674
Iowa | Clinton IA | 6895 | 1019 |  |  | Jackson TN | 3339 | 1404 |  | Leesburg | 5242 | 1189 |  | Wausau | 7821 | 658
Iowa | Council Bluffs | 5864 | 969 |  |  | Knoxville TN | 3959 | 1482 |  | Lynchburg | 4239 | 1305 | Wyoming | Casper | 7409 | 440
Iowa | Creston | 6150 | 983 |  |  | Memphis | 2999 | 2134 |  | Manassas | 5160 | 935 |  | Cheyenne | 7362 | 265
Iowa | Decorah | 6125 | 978 |  |  | Nashville | 3737 | 1751 |  | Marion VA | 4817 | 744 |  | Cody | 7131 | 436
Iowa | Denison | 6571 | 1057 |  | Texas | Abilene | 2968 | 2302 |  | Martinsville | 4496 | 1133 |  | Evanston | 8339 | 188
Iowa | Des Moines | 6493 | 1121 |  |  | Alice | 912 | 4033 |  | Melfa | 3857 | 1387 |  | Gillette | 6992 | 767
Iowa | Dubuque | 7516 | 525 |  |  | Amarillo | 4130 | 1412 |  | Newport News | 3436 | 1705 |  | Jackson Hole | 9670 | 15
Iowa | Estherville | 8458 | 551 |  |  | Austin TX | 1269 | 2884 |  | Norfolk VA | 3411 | 1630 |  | Lander | 7477 | 432
Iowa | Fairfield IA | 6031 | 1093 |  |  | Brownsville | 750 | 3867 |  | Petersburg VA | 3557 | 1400 |  | Laramie | 7799 | 111
Iowa | Fort Dodge | 7177 | 825 |  |  | Childress | 3258 | 2007 |  | Pulaski | 3336 | 1539 |  | Rawlins | 7392 | 289
Iowa | Fort Madison | 5277 | 1148 |  |  | College Station | 1646 | 2670 |  | Quantico | 4109 | 1232 |  | Riverton | 7579 | 708
Iowa | Keokuk | 5496 | 1208 |  |  | Corpus Christi | 934 | 3313 |  | Richmond | 3883 | 1493 |  | Rock Springs | 7971 | 191
Iowa | Knoxville IA | 5891 | 1265 |  |  | Cotulla | 918 | 3848 |  | Roanoke | 4246 | 1552 |  | Sheridan | 7215 | 399
Iowa | Le Mars | 6122 | 871 |  |  | Dalhart | 5029 | 1041 |  | Virginia Beach | 3336 | 1539 |  | Worland | 7285 | 611
Iowa | Mason City | 7927 | 639 |  | City: Dallas; HDD: 2333; CDD: 2678; City: Washington DC; HDD: 4921; CDD: 1113
Iowa | Monticello IA | 6857 | 744
Iowa | Muscatine | 6206 | 1026
Iowa | Newton IA | 6207 | 816
Iowa | Oelwen | 6483 | 644
Iowa | Orange City | 6867 | 865
Iowa | Ottumwa | 6647 | 875
Iowa | Red Oak | 5959 | 1203
Iowa | Sheldon | 6939 | 723
Iowa | Shenandoah | 6233 | 1258
Iowa | Sioux City | 6796 | 936
Iowa | Spencer | 8206 | 592
Iowa | Storm Lake | 6982 | 821
Iowa | Washington IA | 6249 | 991
Iowa | Waterloo | 7257 | 827
Iowa | Webster City | 6376 | 1099
Kansas | Chanute | 4458 | 1804
Kansas | Concordia | 4890 | 1632
Kansas | Dodge City | 4969 | 1457
Kansas | Emporia | 5717 | 1458
Kansas | Garden City | 5180 | 1240
Kansas | Goodland | 5915 | 915
Kansas | Great Bend | 4891.5 | 1417
Kansas | Hays | 5021 | 1558
Kansas | Hill City | 5597 | 1192
Kansas | Hutchinson KS | 4591 | 1552
Kansas | Junction City | 4528 | 1600
Kansas | Liberal | 4810 | 1410
Kansas | Manhattan | 5013 | 1652
Kansas | Newton KS | 5023 | 1400
Kansas | Olathe | 4598 | 1437
Kansas | Russell | 5005 | 1436
Kansas | Salina | 4660 | 1787
Kansas | Topeka | 4953 | 1315
Kansas | Wichita | 4324 | 1554
Kentucky | Bowling Green | 4380 | 1410
Kentucky | Fort Knox | 4918 | 1283
Kentucky | Hebron | 5288 | 962
Kentucky | Henderson City | 5049 | 995
Kentucky | Hopkinsville | 4484 | 1620
Kentucky | Jackson KY | 3869 | 1098
Kentucky | Lexington | 4856 | 1104
Kentucky | London | 4529 | 988
Kentucky | Louisville | 4521 | 1449
Kentucky | Somerset | 3916 | 1550
Kentucky | West Paducah | 3811 | 1439
Louisiana | Alexandria LA | 1136 | 2477
Louisiana | Baton Rouge | 1762 | 2622
Louisiana | Bossier City | 2562 | 2270
Louisiana | Houma | 1677 | 2848
Louisiana | Lafayette LA | 1590 | 2699
Louisiana | Lake Charles | 1635 | 2596
Louisiana | Leesville | 2197 | 2514
Louisiana | Monroe | 2229 | 2270
Louisiana | New Iberia | 1717 | 2559
Louisiana | New Orleans | 1358 | 2784
Louisiana | Patterson | 1452 | 2571
Louisiana | Pineville | 2109 | 2421
Louisiana | Shreveport | 2351 | 2384
Maine | Auburn ME | 7691 | 303
Maine | Augusta ME | 7495 | 396
Maine | Bangor | 7671 | 450
Maine | Bar Harbor | 8037 | 71
Maine | Brunswick ME | 7456 | 373
Maine | Caribou | 9841 | 171
Maine | Frenchville | 9765 | 164
Maine | Houlton | 9255 | 206
Maine | Millinocket | 7921 | 323
Maine | Portland ME | 7679 | 335
Maine | Presque Isle | 9295 | 168
Maine | Rockland | 7451 | 194
Maine | Sanford | 7774 | 259
Maine | Waterville | 7926 | 367
Maine | Wiscasset | 6877 | 350
Maryland | Baltimore | 4631 | 1237
Maryland | Camp Springs | 4652 | 1178
Maryland | Hagerstown | 4867 | 1079
Maryland | Lexington Park | 3556 | 1404
Maryland | Salisbury | 3910 | 1229
Massachusetts | Beverly | 6669 | 492
Massachusetts | Boston | 5793 | 734
Massachusetts | Chicopee Falls | 6354 | 507
Massachusetts | Hyannis | 5749 | 436
Massachusetts | Lawrence | 5940 | 559
Massachusetts | Marthas Vineyard | 5622 | 361
Massachusetts | Mashpee | 6062 | 565
Massachusetts | Nantucket | 5350 | 298
Massachusetts | New Bedford | 5724 | 577
Massachusetts | North Adams | 6626 | 319
Massachusetts | Norwood | 6177 | 637
Massachusetts | Plymouth | 5889 | 374
Massachusetts | Provincetown | 5705 | 595
Massachusetts | Westfield | 6623 | 494
Massachusetts | Worchester | 7164 | 346
Michigan | Alpena | 8250 | 290
Michigan | Ann Arbor | 6487 | 492
Michigan | Battle Creek | 6210 | 639
Michigan | Benton Harbor | 6588 | 810
Michigan | Cadillac | 7905 | 373
Michigan | Calumet | 8988 | 239
Michigan | Detroit | 6621 | 679
Michigan | Escanaba | 8796 | 131
Michigan | Flint | 6977 | 515
Michigan | Freeland | 7059 | 524
Michigan | Grand Rapids MI | 6908 | 579
Michigan | Houghton Lake | 8067 | 316
Michigan | Howell | 6295 | 899
Michigan | Ironwood | 9090 | 348
Michigan | Jackson MI | 6385 | 715
Michigan | Kalamazoo | 6196 | 599
Michigan | Kincheloe | 9193 | 115
Michigan | Kingsford | 8327 | 432
Michigan | Lansing | 7045 | 597
Michigan | Manistee | 7343 | 582
Michigan | Marie | 9162 | 113
Michigan | Menominee | 7783 | 452
Michigan | Mount Clemens | 6040 | 597
Michigan | Muskegon | 7018 | 502
Michigan | Oscoda | 7315 | 455
Michigan | Pellston | 7426 | 360
Michigan | Port Huron | 6522 | 705
Michigan | Traverse City | 7754 | 370
Michigan | Waterford Township | 6152 | 772
Minnesota | Aitkin | 9304 | 194
Minnesota | Albert Lea | 7196 | 920
Minnesota | Alexandria MN | 8895 | 535
Minnesota | Austin MN | 7892 | 529
Minnesota | Baudette | 8804 | 112
Minnesota | Bemidji | 9161 | 333
Minnesota | Benson | 8676 | 659
Minnesota | Brainerd | 8713 | 322
Minnesota | Cambridge | 8823 | 405
Minnesota | Cloquet | 9368 | 258
Minnesota | Crane Lake | 10240 | 164
Minnesota | Crookston | 9095 | 348
Minnesota | Detroit Lakes | 8704 | 460
Minnesota | Duluth | 9620 | 159
Minnesota | Ely | 9501 | 186
Minnesota | Eveleth | 9987 | 255
Minnesota | Fairmont | 7586 | 652
Minnesota | Faribault | 7497 | 504
Minnesota | Fergus Falls | 7838 | 841
Minnesota | Flying Cloud | 7921 | 958
Minnesota | Fosston | 9746 | 252
Minnesota | Glenwood | 8440 | 528
Minnesota | Grand Rapids MN | 9137 | 306
Minnesota | Hallock | 9445 | 460
Minnesota | Hibbing | 9987 | 219
Minnesota | Hutchinson MN | 8330 | 620
Minnesota | International Falls | 10382 | 259
Minnesota | Litchfield | 7734 | 543
Minnesota | Little Falls | 9240 | 385
Minnesota | Mankato | 7716 | 645
Minnesota | Marshall | 7740 | 688
Minnesota | Minneapolis | 7783 | 731
Minnesota | Mora | 8665 | 364
Minnesota | Morris | 8849 | 375
Minnesota | New Ulm | 7646 | 641
Minnesota | Orr | 10534 | 152
Minnesota | Owatonna | 7788 | 641
Minnesota | Park Rapids | 9215 | 236
Minnesota | Pipestone | 8624 | 649
Minnesota | Red Wing | 7935 | 761
Minnesota | Redwood Falls | 7938 | 609
Minnesota | Rochester | 8386 | 488
Minnesota | Roseau | 9817 | 162
Minnesota | Silver Bay | 10453 | 59
Minnesota | St Cloud | 9020 | 444
Minnesota | St Paul | 8019 | 587
Minnesota | Thief River Falls | 9328 | 341
Minnesota | Two Harbors | 9412 | 190
Minnesota | Wheaton | 8713 | 496
Minnesota | Willmar | 7649 | 581
Minnesota | Winona | 7711 | 633
Minnesota | Worthington | 7750 | 644
Mississippi | Biloxi | 1928 | 2606
Mississippi | Columbus MS | 3394 | 2077
Mississippi | Greenville MS | 2432 | 2468
Mississippi | Greenwood | 2552 | 2164
Mississippi | Gulfport | 1619 | 2565
Mississippi | Hattiesburg | 2274 | 2071
Mississippi | Jackson MS | 2428 | 2237
Mississippi | McComb | 2086 | 2315
Mississippi | Meridian | 2417 | 2038
Mississippi | Natchez | 1915 | 2060
Mississippi | Starkville | 3378 | 1962
Mississippi | Tupelo | 3039 | 1905
Missouri | Cape Girardeau | 4506 | 1289
Missouri | Columbia MO | 5307 | 1190
Missouri | Farmington MO | 4527 | 1190
Missouri | Ft. Leonard Wood | 4675 | 1496
Missouri | Jefferson City | 4504 | 1469
Missouri | Joplin | 3663 | 1949
Missouri | Kaiser | 4634 | 1528
Missouri | Kansas City | 5434 | 1316
Missouri | Kirksville | 6397 | 1047
Missouri | Poplar Bluff | 4108 | 1592
Missouri | Springfield MO | 4629 | 1307
Missouri | St. Joseph | 5495 | 1379
Missouri | St. Louis | 4846 | 1555
Missouri | Vichy | 4729 | 924
Missouri | Warrensburg | 4803 | 1344
Montana | Billings | 6731 | 548
Montana | Bozeman | 8354 | 282
Montana | Butte | 9089 | 101
Montana | Cut Bank | 8186 | 86
Montana | Glasgow | 8163 | 504
Montana | Glendive | 8667 | 555
Montana | Great Falls | 7854 | 344
Montana | Havre | 8213 | 432
Montana | Helena | 7587 | 320
Montana | Kalispell | 7928 | 126
Montana | Lewistown | 8014 | 107
Montana | Livingston | 7111 | 370
Montana | Miles City | 7617 | 648
Montana | Missoula | 7323 | 269
Montana | Sidney MT | 9396 | 411
Montana | Wolf Point | 8983 | 249
Nebraska | Ainsworth | 6118 | 789
Nebraska | Alliance | 7026 | 736
Nebraska | Beatrice | 5646 | 1135
Nebraska | Bellevue | 6309 | 1139
Nebraska | Broken Bow | 6772 | 790
Nebraska | Chadron | 6543 | 812
Nebraska | Columbus NC | 6670 | 937
Nebraska | Falls City | 5775 | 1039
Nebraska | Fremont | 6953 | 935
Nebraska | Grand Island | 6654 | 1041
Nebraska | Hastings | 6075 | 1108
Nebraska | Holdrege | 6510 | 852
Nebraska | Imperial NE | 5834 | 1024
Nebraska | Kearney | 6348 | 843
Nebraska | Lincoln | 5892 | 1220
Nebraska | McCook | 5616 | 1256
Nebraska | Norfolk NE | 6943 | 986
Nebraska | North Platte | 6556 | 802
Nebraska | Omaha | 5954 | 1275
Nebraska | O'Neill | 7733 | 847
Nebraska | Ord | 6279 | 872
Nebraska | Scottsbluff | 6560 | 760
Nebraska | Sidney NE | 6864 | 494
Nebraska | Tekamah | 6650 | 1005
Nebraska | Valentine | 6453 | 811
Nevada | Elko | 7070 | 407
Nevada | Ely | 7267 | 154
Nevada | Fallon | 5163 | 1010
Nevada | Las Vegas NV | 2301 | 3187
Nevada | Lovelock | 5351 | 836
Nevada | Mercury | 3001 | 2396
Nevada | Reno | 5488 | 620
Nevada | Tonopah | 5431 | 747
Nevada | Winnemucca | 6158 | 567
New Hampshire | Berlin | 8891 | 145
New Hampshire | Concord NH | 7479 | 397
New Hampshire | Keene | 7169 | 470
New Hampshire | Laconia | 7198 | 396
New Hampshire | Lebanon | 7349 | 389
New Hampshire | Manchester | 6322 | 664
New Hampshire | Mount Washington | 13275 | 0
New Hampshire | Portsmouth | 6753 | 527
New Jersey | Atlantic City | 5073 | 886
New Jersey | Belmar | 5280 | 890
New Jersey | Fairfield NJ | 5060 | 654
New Jersey | Millville | 4680 | 1011
New Jersey | Newark | 5057 | 1237
New Jersey | Rio Grande | 4286 | 1028
New Jersey | Teterboro | 4868 | 695
New Jersey | Trenton | 5040 | 1177
New Mexico | Alamogordo | 3327 | 1793
New Mexico | Albuquerque | 4157 | 1269
New Mexico | Carlsbad NM | 2764 | 2298
New Mexico | Clayton | 4765 | 1156
New Mexico | Clovis | 4467 | 1396
New Mexico | Deming | 2878 | 1891
New Mexico | Farmington NM | 5199 | 1022
New Mexico | Gallup | 6002 | 388
New Mexico | Las Cruces | 2876 | 2146
New Mexico | Las Vegas NM | 5180 | 307
New Mexico | Roswell | 2735 | 1932
New Mexico | Ruidoso | 4095 | 604
New Mexico | Santa Fe | 5449 | 589
New Mexico | Taos | 6904 | 198
New Mexico | Truth or Consequences | 3102 | 1742
New Mexico | Tucumcari | 4109 | 1423
New York | Albany NY | 6773 | 489
New York | Binghamton | 7015 | 404
New York | Buffalo | 6612 | 468
New York | Elmira | 6449 | 297
New York | Glen Falls | 7158 | 481
New York | Jamestown NY | 7188 | 278
New York | Massena | 8046 | 376
New York | Monticello NY | 7059 | 428
New York | New Windsor | 6159 | 756
New York | New York | 4885 | 1133
New York | Nigara Falls | 6484 | 602
New York | Republic | 4893 | 983
New York | Rockester | 6518 | 627
New York | Ronkonkoma | 5005 | 983
New York | Saranac Lake | 9158 | 149
New York | Syracuse | 6609 | 535
New York | Utica | 6974 | 414
New York | Wappingers Falls | 6030 | 607
New York | Watertown NY | 7496 | 330
New York | Westhampton Beach | 5741 | 455
New York | White Plains | 5783 | 595
North Carolina | Asheville | 4273 | 817
North Carolina | Cape Hatteras | 2563 | 1729
North Carolina | Charlotte | 3153 | 1675
North Carolina | Elizabeth City | 2744 | 1760
North Carolina | Fayetteville NC | 3489 | 1576
North Carolina | Goldsboro | 3589 | 1743
North Carolina | Greensboro | 3868 | 1371
North Carolina | Greenville NC | 3040 | 1603
North Carolina | Havelock | 3345 | 1701
North Carolina | Hickory | 3457 | 1416
North Carolina | Jacksonville NC | 3814 | 1370
North Carolina | Kinston | 3397 | 1818
North Carolina | Manteo | 3053 | 1617
North Carolina | New Bern | 2276 | 1874
North Carolina | Raleigh | 3465 | 1566
North Carolina | Rocky Mount | 2878 | 1435
North Carolina | Southern Pines | 3570 | 1496
North Carolina | Wilmington NC | 2401 | 1928
North Carolina | Winston-Salem | 3214 | 1244
North Dakota | Bismarck | 8452 | 453
North Dakota | Devils Lake | 9251 | 288
North Dakota | Dickinson | 9028 | 417
North Dakota | Fargo | 9211 | 491
North Dakota | Grand Forks | 9534 | 486
North Dakota | Jamestown ND | 9505 | 519
North Dakota | Minot | 8972 | 432
North Dakota | Williston | 8467 | 404
Ohio | Akron OH | 259 | 654
Ohio | Cincinnati | 4911 | 1039
Ohio | Cleveland | 6160 | 760
Ohio | Columbus OH | 5599 | 747
Ohio | Dayton | 5945 | 905
Ohio | Findlay | 5590 | 541
Ohio | Mansfield | 6615 | 620
Ohio | Toledo OH | 6515 | 610
Ohio | Youngstown | 6628 | 531
Ohio | Zanesville | 4941 | 702
Oklahoma | Altus | 3164 | 2563
Oklahoma | Bartlesville | 4266 | 1654
Oklahoma | Clinton OK | 4175 | 2023
Oklahoma | Enid | 4466 | 2034
Oklahoma | Fort Sill | 3421 | 2392
Oklahoma | Gage | 4103 | 2013
Oklahoma | Hobart | 3600 | 2377
Oklahoma | Lawton | 3055 | 1979
Oklahoma | McAlester | 3081 | 2086
Oklahoma | Oklahoma City | 3556 | 2038
Oklahoma | Ponca City | 3887 | 2437
Oklahoma | Stillwater | 3799 | 2185
Oklahoma | Tulsa | 3844 | 2066
Oregon | Astoria | 4933 | 48
Oregon | Aurora OR | 4277 | 327
Oregon | Baker City | 7142 | 231
Oregon | Burns | 7201 | 230
Oregon | Corvallus | 4257 | 405
Oregon | Eugene | 4803 | 295
Oregon | Klamath Falls | 6765 | 185
Oregon | La Grande | 6152 | 329
Oregon | Lakeview | 7091 | 199
Oregon | Medford | 4530 | 602
Oregon | North Bend | 4525 | 0
Oregon | Pendleton | 5204 | 585
Oregon | Portland OR | 4187 | 367
Oregon | Redmond | 6583 | 204
Oregon | Roseburg | 3798 | 405
Oregon | Salem | 4583 | 275
Oregon | Sexton Summit | 5657 | 362
Pennsylvania | Allentown | 5651 | 773
Pennsylvania | Altoona | 5917 | 595
Pennsylvania | Bradford | 8204 | 204
Pennsylvania | Butler | 6575 | 481
Pennsylvania | DuBois | 6942 | 386
Pennsylvania | Erie | 6460 | 579
Pennsylvania | Franklin PA | 6830 | 327
Pennsylvania | Harrisburg | 5409 | 927
Pennsylvania | Johnstown | 6516 | 482
Pennsylvania | Lancaster PA | 4955 | 877
Pennsylvania | Middletown | 6105 | 1123
Pennsylvania | Philadelphia | 4824 | 1184
Pennsylvania | Pittsburgh | 5925 | 726
Pennsylvania | Reading | 5067 | 900
Pennsylvania | Scranton | 5216 | 608
Pennsylvania | University Park | 6188 | 585
Pennsylvania | Washington PA | 5727 | 528
Pennsylvania | Williamsport | 5761 | 759
Rhode Island | New Shoreham | 5221 | 435
Rhode Island | Pawtucket | 6466 | 504
Rhode Island | Providence | 5870 | 735
South Carolina | Anderson | 3436 | 1037
South Carolina | Beaufort | 2096 | 2158
South Carolina | Charleston SC | 2051 | 2302
South Carolina | Columbia SC | 2593 | 2020
South Carolina | Florence | 2316 | 2202
South Carolina | Greenville SC | 3652 | 1409
South Carolina | Greer | 3244 | 1553
South Carolina | Myrtle Beach | 2379 | 1870
South Carolina | North Myrtle Beach | 2470 | 1727
South Carolina | Sumter | 3072 | 1706
South Dakota | Aberdeen SD | 7968 | 657
South Dakota | Brookings | 7926 | 449
South Dakota | Huron | 8196 | 638
South Dakota | Mitchell | 7879 | 909
South Dakota | Mobridge | 8474 | 735
South Dakota | Pierre | 7079 | 818
South Dakota | Rapid City | 7203 | 675
South Dakota | Sioux Falls | 7680 | 680
South Dakota | Watertown SD | 8803 | 422
South Dakota | Yankton | 7058 | 996
Tennessee | Blountville | 4439 | 971
Tennessee | Chattanooga | 3224 | 1657
Tennessee | Crossville | 3976 | 933
Tennessee | Dyersburg | 3723 | 1896
Tennessee | Jackson TN | 3339 | 1404
Tennessee | Knoxville TN | 3959 | 1482
Tennessee | Memphis | 2999 | 2134
Tennessee | Nashville | 3737 | 1751
Texas | Abilene | 2968 | 2302
Texas | Alice | 912 | 4033
Texas | Amarillo | 4130 | 1412
Texas | Austin TX | 1269 | 2884
Texas | Brownsville | 750 | 3867
Texas | Childress | 3258 | 2007
Texas | College Station | 1646 | 2670
Texas | Corpus Christi | 934 | 3313
Texas | Cotulla | 918 | 3848
Texas | Dalhart | 5029 | 1041
Texas | Dallas | 2333 | 2678
Texas | Del Rio | 1340 | 3187
Texas | El Paso | 2499 | 2171
Texas | Galveston | 1096 | 3116
Texas | Georgetown | 2070 | 2683
Texas | Greenville TX | 2717 | 2445
Texas | Harlingen | 518 | 3816
Texas | Hondo | 1694 | 2825
Texas | Houston | 1439 | 2974
Texas | Killeen | 2087 | 2721
Texas | Kingsville | 895 | 3419
Texas | Laredo | 1164 | 4080
Texas | Longview | 2131 | 2437
Texas | Lubbock | 3436 | 1699
Texas | Lufkin | 1823 | 2479
Texas | Marfa | 3117 | 1044
Texas | McAllen | 729 | 3903
Texas | McGregor | 2334 | 2614
Texas | Midland | 2482 | 2057
Texas | Mineral wells | 2363 | 2495
Texas | Nacogdockes | 2305 | 2313
Texas | Palacios | 1346 | 3024
Texas | Paris | 3100 | 2057
Texas | Port Arthur | 1422 | 2904
Texas | Rockport | 691 | 3576
Texas | San Angelo | 2485 | 2259
Texas | San Antonio | 1548 | 2992
Texas | Temple | 2260 | 2717
Texas | Tyler | 2339 | 2363
Texas | Victoria | 1309 | 3042
Texas | Waco | 2251 | 2699
Texas | Wichita Falls | 2838 | 2350
Texas | Wink | 2423 | 2932
Utah | Blanding | 5535 | 1171
Utah | Bryce Canyon City | 8955 | 33
Utah | Cedar City | 5776 | 747
Utah | Delta | 6021 | 799
Utah | Hanksville | 5354 | 1445
Utah | Moab | 5106 | 1301
Utah | Ogden | 5831 | 1092
Utah | Provo | 5836 | 858
Utah | Saint George | 2729 | 2936
Utah | Salt Lake City | 5350 | 1118
Utah | Vernal | 6661 | 525
Utah | Wendover | 5970 | 1221
Vermont | Burlington VT | 7491 | 420
Vermont | Montpelier | 7662 | 249
Vermont | Rutland | 7563 | 485
Vermont | Springfield VT | 7264 | 281
Virginia | Abingdon | 4953 | 1011
Virginia | Blacksburg | 5081 | 754
Virginia | Charlottesville | 3697 | 1122
Virginia | Danville | 3707 | 1678
Virginia | Farmville | 4084 | 1323
Virginia | Franklin VA | 3096 | 1557
Virginia | Fredericksburg | 4531 | 1420
Virginia | Hampton | 4195 | 1437
Virginia | Hillsville | 5459 | 604
Virginia | Hot Springs VA | 6585 | 254
Virginia | Leesburg | 5242 | 1189
Virginia | Lynchburg | 4239 | 1305
Virginia | Manassas | 5160 | 935
Virginia | Marion VA | 4817 | 744
Virginia | Martinsville | 4496 | 1133
Virginia | Melfa | 3857 | 1387
Virginia | Newport News | 3436 | 1705
Virginia | Norfolk VA | 3411 | 1630
Virginia | Petersburg VA | 3557 | 1400
Virginia | Pulaski | 3336 | 1539
Virginia | Quantico | 4109 | 1232
Virginia | Richmond | 3883 | 1493
Virginia | Roanoke | 4246 | 1552
Virginia | Virginia Beach | 3336 | 1539
Virginia | Washington DC | 4921 | 1113
Virginia | Weyers Cave | 4878 | 1102
Virginia | Winchester | 5193 | 1196
Virginia | Wise | 4910 | 747
Washington | Aberdeen WA | 5240 | 21
Washington | Bellingham | 5768 | 24
Washington | Bremerton | 5533 | 112
Washington | Ephrata | 5578 | 882
Washington | Everett | 5097 | 69
Washington | Forks | 5682 | 19
Washington | Hanford | 5669 | 1007
Washington | Hoquiam | 5240 | 21
Washington | Kelso | 4682 | 115
Washington | Moses Lake | 5431 | 641
Washington | Olympia | 5331 | 118
Washington | Pasco | 4921 | 711
Washington | Port Angeles | 5945 | 13
Washington | Pullman | 6483 | 234
Washington | Renton | 4378 | 216
Washington | Seattle | 4372 | 169
Washington | Spokane | 6716 | 341
Washington | Stampede Pass | 8898 | 81
Washington | Tacoma | 5664 | 142
Washington | The Dalles | 4501 | 879
Washington | Toledo WA | 5853 | 82
Washington | Walla Walla | 4836 | 839
Washington | Wenatchee | 5748 | 867
Washington | Whidbey Island | 5510 | 0
Washington | Yakima | 6041 | 430
West Virginia | Beckley | 5361 | 631
West Virginia | Bluefield | 4451 | 597
West Virginia | Bridgeport | 5137 | 855
West Virginia | Charleston WV | 4708 | 1015
West Virginia | Elkins | 6050 | 368
West Virginia | Huntington | 4642 | 1077
West Virginia | Lewisburg | 6270 | 432
West Virginia | Martinsburg | 4345 | 761
West Virginia | Morgantown | 5020 | 669
West Virginia | Parkersburg | 4979 | 1101
West Virginia | Wheeling | 5793 | 639
Wisconsin | Antigo | 8664 | 440
Wisconsin | Appleton | 7022 | 517
Wisconsin | Eau Claire | 8475 | 600
Wisconsin | Green Bay | 7853 | 496
Wisconsin | Janesville | 6713 | 295
Wisconsin | La Crosse | 7445 | 748
Wisconsin | Lone Rock | 6651 | 543
Wisconsin | Madison | 7724 | 604
Wisconsin | Manitowac | 7231 | 322
Wisconsin | Marshfield | 7449 | 432
Wisconsin | Milwaukee | 7348 | 545
Wisconsin | Minocqua | 8772 | 410
Wisconsin | Mosinee | 8719 | 401
Wisconsin | Oshkosh | 8013 | 380
Wisconsin | Phillips | 8638 | 337
Wisconsin | Rhinelander | 8823 | 437
Wisconsin | Rice Lake | 8706 | 420
Wisconsin | Sturgeon Bay | 7301 | 424
Wisconsin | Watertown WI | 6864 | 674
Wisconsin | Wausau | 7821 | 658
Wyoming | Casper | 7409 | 440
Wyoming | Cheyenne | 7362 | 265
Wyoming | Cody | 7131 | 436
Wyoming | Evanston | 8339 | 188
Wyoming | Gillette | 6992 | 767
Wyoming | Jackson Hole | 9670 | 15
Wyoming | Lander | 7477 | 432
Wyoming | Laramie | 7799 | 111
Wyoming | Rawlins | 7392 | 289
Wyoming | Riverton | 7579 | 708
Wyoming | Rock Springs | 7971 | 191
Wyoming | Sheridan | 7215 | 399
Wyoming | Worland | 7285 | 611